## 119_1
S&C Power Fuses - Types SMD-1A, -2B, -2C, -3, and -50 | [9 empty] | S&C Power Fuses - Types SMD-1A, -2B, -2C, -3, and -50 | [9 empty] | S&C Power Fuses - Types SMD-1A, -2B, -2C, -3, and -50 | [9 empty] | S&C Power Fuses - Types SMD-1A, -2B, -2C, -3, and -50
Slow Speed (TCC 119-1) | [9 empty] | Slow Speed (TCC 119-1) | [9 empty] | Slow Speed (TCC 119-1) | [9 empty] | Slow Speed (TCC 119-1)
Minimum Melting Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated August 29, 1988
Tolerance in Terms of Current: Plus 10% | [9 empty] | Tolerance in Terms of Current: Plus 10% | [9 empty] | Tolerance in Terms of Current: Plus 10% | [9 empty] | Tolerance in Terms of Current: Plus 10%
15E |  | 20E |  | 25E |  | 30E |  | 40E |  | 50E |  | 65E |  | 80E |  | 100E |  | 125E |  | 150E |  | 175E |  | 200E |  | 250E |  | 300E |  | 2-200E |  | 2-250E |  | 2-300E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
930.694 | 0.01 | 1178.42 | 0.01 | 1359.57 | 0.01 | 1782.78 | 0.01 | 2596.52 | 0.01 | 3284.36 | 0.01 | 3943.91 | 0.01 | 5213.09 | 0.01 | 6713.85 | 0.01 | 8450.05 | 0.01 | 10624.6 | 0.01 | 11648.4 | 0.01 | 13452.6 | 0.01 | 16779.7 | 0.01 | 20908.8 | 0.01 | 24512.2 | 0.01 | 28880.6 | 0.01 | 37381.3 | 0.01
881.77 | 0.011107 | 1122.07 | 0.01103 | 1324.68 | 0.010555 | 1747.48 | 0.010419 | 2527.35 | 0.010555 | 3212.9 | 0.010429 | 3877.43 | 0.010377 | 5023.73 | 0.010714 | 6607.29 | 0.010356 | 5664.24 | 0.022233 | 7722.77 | 0.018908 | 8037.94 | 0.021043 | 9460.95 | 0.020077 | 11883.7 | 0.019917 | 15977.3 | 0.017092 | 16186.4 | 0.02275 | 20109 | 0.020483 | 27417.2 | 0.018515
805.877 | 0.013311 | 1040.99 | 0.012815 | 1250.04 | 0.011829 | 1677.28 | 0.01132 | 2413.73 | 0.011549 | 3111.71 | 0.011107 | 3740.33 | 0.011174 | 4807.48 | 0.011794 | 6348.21 | 0.01123 | 4141.98 | 0.041662 | 5744.1 | 0.03394 | 5647.27 | 0.042419 | 6548.09 | 0.041871 | 8399.5 | 0.039789 | 11601.9 | 0.03222 | 10785.1 | 0.050784 | 14471.3 | 0.039511 | 19320.6 | 0.03736
746.153 | 0.015481 | 964.81 | 0.014918 | 1177.24 | 0.013364 | 1603.47 | 0.012386 | 2286.84 | 0.01284 | 2965.88 | 0.012214 | 3597.26 | 0.012068 | 4582.17 | 0.01293 | 6038.6 | 0.012374 | 3206.48 | 0.069241 | 4341.3 | 0.059299 | 4100.76 | 0.080607 | 4817.1 | 0.076753 | 6032.57 | 0.076906 | 8716.11 | 0.057317 | 7434.81 | 0.10591 | 10136.8 | 0.081092 | 13372.1 | 0.077835
696.405 | 0.017789 | 887.076 | 0.017665 | 1083.47 | 0.015762 | 1517.66 | 0.013854 | 2162.3 | 0.014333 | 2795.95 | 0.013744 | 3401.35 | 0.013485 | 4354.34 | 0.01429 | 5761.36 | 0.013634 | 2375.42 | 0.12604 | 3074.59 | 0.11787 | 3158.74 | 0.13518 | 3327.34 | 0.16023 | 4460.11 | 0.14112 | 6687.05 | 0.097182 | 5647.27 | 0.18467 | 7434.81 | 0.15074 | 9690.76 | 0.1494
637.74 | 0.021212 | 806.683 | 0.021361 | 1001.17 | 0.018478 | 1419.31 | 0.015793 | 2024.2 | 0.016389 | 2648.98 | 0.015327 | 3222.55 | 0.015023 | 4092.57 | 0.016193 | 5318.4 | 0.016 | 1756.24 | 0.23058 | 2219.26 | 0.22399 | 2382.55 | 0.23784 | 2425.83 | 0.30024 | 3404.75 | 0.23975 | 5291.88 | 0.15565 | 4415.73 | 0.30205 | 5778.67 | 0.25229 | 7375.57 | 0.2605
577.051 | 0.025857 | 734.31 | 0.02578 | 886.19 | 0.023679 | 1322.03 | 0.018276 | 1883.58 | 0.018908 | 2489.73 | 0.01735 | 3056.2 | 0.01672 | 3858.09 | 0.018331 | 4998.68 | 0.018167 | 1303.65 | 0.42692 | 1592.29 | 0.43948 | 1900.61 | 0.37713 | 1743.98 | 0.58792 | 2732.38 | 0.37338 | 4393.71 | 0.22851 | 3284.36 | 0.5449 | 4802.67 | 0.36929 | 5458.49 | 0.47991
521.094 | 0.031772 | 677.176 | 0.030313 | 776.604 | 0.030618 | 1227.74 | 0.021255 | 1768.57 | 0.021511 | 2335.38 | 0.019719 | 2886.87 | 0.018739 | 3622.53 | 0.020709 | 4702.87 | 0.020462 | 1050.4 | 0.67763 | 1210.67 | 0.77247 | 1528.32 | 0.59324 | 1370.49 | 0.96642 | 2230.38 | 0.56827 | 3470.06 | 0.3745 | 2633.13 | 0.8503 | 3858.09 | 0.59146 | 4518.47 | 0.71451
463.558 | 0.039948 | 623.863 | 0.035751 | 692.931 | 0.038652 | 1152.77 | 0.024206 | 1650.66 | 0.024695 | 2186.22 | 0.022547 | 2737.85 | 0.020855 | 3374.25 | 0.023941 | 4393.71 | 0.023514 | 879.128 | 0.99585 | 992.206 | 1.1839 | 1270.2 | 0.87971 | 1141.3 | 1.4345 | 1816.97 | 0.87533 | 2729.65 | 0.61683 | 2160.14 | 1.2838 | 3235.47 | 0.86402 | 3865.82 | 0.99784
415.686 | 0.049729 | 579.944 | 0.04133 | 630.133 | 0.046693 | 1064.14 | 0.028377 | 1535.99 | 0.028434 | 2038.42 | 0.025909 | 2552.75 | 0.023893 | 3155.58 | 0.027346 | 4141.98 | 0.026432 | 758.946 | 1.3935 | 797.858 | 1.9191 | 1083.47 | 1.2409 | 1018.34 | 1.8568 | 1539.06 | 1.2509 | 2151.52 | 1.0231 | 1846.28 | 1.8019 | 2754.33 | 1.2397 | 3370.88 | 1.3632
375.002 | 0.060983 | 533.218 | 0.048891 | 568.46 | 0.057431 | 987.257 | 0.032937 | 1416.48 | 0.033368 | 1910.13 | 0.029506 | 2399.29 | 0.027129 | 2942.25 | 0.031487 | 3774.14 | 0.031868 | 670.438 | 1.8623 | 695.709 | 2.6534 | 936.295 | 1.714 | 911.353 | 2.4396 | 1331.32 | 1.7261 | 1872.31 | 1.4019 | 1605.08 | 2.5189 | 2423.4 | 1.67 | 2956.99 | 1.8568
329.287 | 0.078932 | 487.325 | 0.058709 | 510.265 | 0.071207 | 894.201 | 0.040108 | 1303.65 | 0.039236 | 1761.51 | 0.03466 | 2192.79 | 0.032446 | 2702.49 | 0.037248 | 3483.97 | 0.037434 | 586.945 | 2.5776 | 629.503 | 3.431 | 822.157 | 2.3323 | 825.452 | 3.1357 | 1181.96 | 2.2998 | 1619.59 | 1.9696 | 1420.73 | 3.3968 | 2111.02 | 2.344 | 2662.25 | 2.4178
300.345 | 0.094878 | 451.661 | 0.06821 | 461.707 | 0.087146 | 811.538 | 0.048891 | 1197.42 | 0.046506 | 1624.45 | 0.040837 | 2018.13 | 0.038305 | 2494.71 | 0.043754 | 3258.19 | 0.042802 | 521.616 | 3.4793 | 570.738 | 4.4855 | 735.044 | 3.1294 | 752.899 | 4.0142 | 1059.9 | 3.0248 | 1405.19 | 2.8062 | 1282.96 | 4.481 | 1857.39 | 3.313 | 2358.85 | 3.2898
266.648 | 0.12049 | 415.271 | 0.080446 | 431.355 | 0.099842 | 721.932 | 0.061472 | 1099.85 | 0.054959 | 1511.61 | 0.047256 | 1887.35 | 0.04393 | 2316.77 | 0.050632 | 3013.71 | 0.050028 | 471.506 | 4.5944 | 513.85 | 6.0973 | 659.796 | 4.1906 | 701.297 | 4.9424 | 963.845 | 3.9112 | 1213.09 | 4.1614 | 1184.32 | 5.6511 | 1694.14 | 4.2967 | 2117.37 | 4.4275
230.888 | 0.16007 | 379.15 | 0.096794 | 400.988 | 0.11542 | 665.096 | 0.072718 | 1027.54 | 0.062966 | 1417.89 | 0.053709 | 1726.63 | 0.052331 | 2115.25 | 0.060678 | 2818.41 | 0.057374 | 430.493 | 6.0125 | 469.623 | 8.1486 | 598.802 | 5.5669 | 649.323 | 6.3334 | 881.77 | 5.0675 | 1096.55 | 5.5836 | 1116.47 | 6.9299 | 1551.42 | 5.6229 | 1948.72 | 5.6851
201.528 | 0.21052 | 345.479 | 0.11693 | 363.919 | 0.13985 | 612.734 | 0.086193 | 944.76 | 0.074559 | 1324.68 | 0.061411 | 1578.02 | 0.062714 | 1929.33 | 0.072718 | 2617.38 | 0.066393 | 392.655 | 8.0353 | 442.275 | 10.1436 | 546.717 | 7.4921 | 613.961 | 7.7667 | 818.056 | 6.3525 | 982.333 | 7.9952 | 1044.12 | 8.8361 | 1423.58 | 7.6741 | 1809.72 | 7.1983
181.804 | 0.2579 | 313.855 | 0.14055 | 330.938 | 0.16878 | 559.997 | 0.10268 | 880.008 | 0.085849 | 1236.36 | 0.070287 | 1453.79 | 0.073743 | 1766.8 | 0.087059 | 2333.04 | 0.083562 | 365.378 | 10.5049 | 421.126 | 12.539 | 505.694 | 10.0728 | 581.686 | 9.6682 | 765.042 | 7.9713 | 906.808 | 10.7171 | 985.285 | 11.5403 | 1303.65 | 10.9665 | 1678.96 | 9.572
162.379 | 0.3246 | 287.416 | 0.16794 | 303.971 | 0.20006 | 504.683 | 0.12629 | 819.694 | 0.098849 | 1142.45 | 0.081907 | 1333.99 | 0.087408 | 1613.12 | 0.10433 | 2149.37 | 0.098454 | 344.444 | 13.5291 | 402.193 | 15.9083 | 476.721 | 13.0638 | 552.211 | 12.1806 | 723.377 | 9.8635 | 855.709 | 13.83 | 939.108 | 15.0269 | 1211.88 | 15.5311 | 1551.42 | 13.6378
148.254 | 0.38862 | 264.524 | 0.19787 | 277.808 | 0.23927 | 460.785 | 0.1515 | 762.75 | 0.11393 | 1056.72 | 0.096312 | 1258.82 | 0.098553 | 1480.19 | 0.12305 | 1966.34 | 0.11764 | 329.617 | 17.0618 | 385.265 | 20.694 | 443.604 | 18.894 | 524.755 | 16.1649 | 690.165 | 12.1441 | 812.35 | 18.2077 | 899.583 | 20.2437 | 1126.56 | 23.947 | 1453.79 | 18.894
136.583 | 0.45787 | 242.24 | 0.23665 | 255.426 | 0.28389 | 409.498 | 0.19106 | 702.701 | 0.1337 | 982.333 | 0.11101 | 1179.6 | 0.11201 | 1367.76 | 0.14411 | 1807.91 | 0.13902 | 318.28 | 21.7986 | 370.529 | 27.5457 | 420.284 | 27.2989 | 498.165 | 23.0541 | 655.194 | 15.7029 | 774.278 | 25.5809 | 859.139 | 29.5134 | 1068.41 | 34.9475 | 1375.99 | 26.7583
127.094 | 0.53091 | 224.962 | 0.27385 | 235.081 | 0.33382 | 369.419 | 0.235 | 656.505 | 0.15364 | 916.838 | 0.12794 | 1108.68 | 0.12705 | 1265.13 | 0.16743 | 1660.59 | 0.16428 | 306.106 | 29.3369 | 354.579 | 41.2994 | 403.805 | 41.1756 | 478.632 | 33.0112 | 630.133 | 20.0022 | 740.948 | 39.6403 | 825.452 | 46.4719 | 1018.34 | 56.7042 | 1307.57 | 39.5611
110.27 | 0.70528 | 206.424 | 0.3246 | 217.224 | 0.39135 | 345.133 | 0.27005 | 607.852 | 0.17958 | 842.97 | 0.1509 | 1040.99 | 0.14397 | 1163.2 | 0.19826 | 1560.76 | 0.18597 | 293.222 | 44.6497 | 342.041 | 62.7305 | 390.697 | 69.1203 | 461.707 | 49.247 | 603.612 | 27.7947 | 715.464 | 60.3915 | 805.877 | 72.5916 | 990.224 | 94.8076 | 1250.04 | 61.8584
98.0947 | 0.8948 | 188.846 | 0.38706 | 203.961 | 0.44479 | 309.492 | 0.33515 | 566.757 | 0.20615 | 743.175 | 0.19356 | 971.587 | 0.16511 | 1072.69 | 0.23243 | 1426.43 | 0.2222 | 283.988 | 68.7068 | 334.933 | 98.9733 | 385.265 | 117.43 | 450.308 | 74.5782 | 583.434 | 39.0892 | 693.625 | 96.7228 | 791.501 | 132.8 | 982.333 | 173.964 | 1204.63 | 103.425
88.6711 | 1.0984 | 172.075 | 0.46479 | 191.508 | 0.5025 | 281.162 | 0.40691 | 523.706 | 0.24071 | 668.43 | 0.23951 | 895.096 | 0.19473 | 995.187 | 0.26897 | 1344.7 | 0.25003 | 277.808 | 96.7228 | 329.617 | 191.493 | 382.577 | 227.204 | 442.275 | 129.781 | 567.324 | 54.8086 | 671.78 | 194.387 | 782.842 | 263.183 | 982.333 | 495.641 | 1177.24 | 189.208
81.2015 | 1.3256 | 150.796 | 0.61314 | 179.098 | 0.57169 | 262.154 | 0.46853 | 492.223 | 0.27249 | 607.852 | 0.28847 | 840.444 | 0.22087 | 928.835 | 0.30815 | 1275.29 | 0.27911 | 273.946 | 191.11 | 326.991 | 595.769 | 380.289 | 395.382 | 437.874 | 247.609 | 557.204 | 81.0324 | 653.231 | 594.579 | 781.278 | 497.131 |  |  | 1176.06 | 496.634
73.9903 | 1.6094 | 134.953 | 0.76402 | 162.704 | 0.69408 | 245.901 | 0.52985 | 457.113 | 0.31564 | 550.557 | 0.35093 | 782.842 | 0.25483 | 866.04 | 0.35411 | 1185.51 | 0.32363 | 272.852 | 596.365 |  |  | 379.909 | 596.365 | 435.69 | 592.798 | 549.457 | 134.001
68.37 | 1.9133 | 122.478 | 0.93131 | 151.401 | 0.80319 | 231.813 | 0.59264 | 423.66 | 0.36745 | 499.662 | 0.42735 | 730.647 | 0.29254 | 808.298 | 0.40569 | 1107.57 | 0.373 | [8 empty] | 541.819 | 238.853
63.8754 | 2.2319 | 111.155 | 1.1421 | 141.731 | 0.92389 | 215.063 | 0.68649 | 391.087 | 0.43164 | 455.288 | 0.51419 | 681.933 | 0.3365 | 749.893 | 0.46853 | 1027.54 | 0.43598 | [8 empty] | 540.195 | 594.579
60.276 | 2.5698 | 100.779 | 1.4132 | 132.281 | 1.0702 | 202.134 | 0.78102 | 362.104 | 0.502 | 418.606 | 0.60341 | 639.017 | 0.38321 | 696.405 | 0.54544 | 959.038 | 0.502
56.7658 | 2.9679 | 90.9158 | 1.7804 | 121.989 | 1.2761 | 187.528 | 0.90923 | 334.933 | 0.58324 | 382.577 | 0.71809 | 582.268 | 0.4634 | 657.82 | 0.60886 | 881.77 | 0.598
53.7817 | 3.4002 | 85.024 | 2.0685 | 113.514 | 1.4916 | 176.784 | 1.0272 | 296.169 | 0.74814 | 352.458 | 0.84522 | 529.499 | 0.5643 | 614.575 | 0.69547 | 832.914 | 0.6783
50.6497 | 3.9465 | 79.4346 | 2.4274 | 104.369 | 1.8091 | 166.489 | 1.1651 | 270.678 | 0.89569 | 329.287 | 0.96835 | 483.926 | 0.6817 | 566.191 | 0.82188 | 777.381 | 0.78729
47.4148 | 4.7296 | 74.7339 | 2.809 | 98.6851 | 2.0541 | 158.053 | 1.3045 | 247.629 | 1.0766 | 307.333 | 1.1161 | 452.565 | 0.78572 | 530.559 | 0.93318 | 730.647 | 0.90289
44.6982 | 5.6116 | 70.2411 | 3.2734 | 93.7783 | 2.2929 | 149.296 | 1.4738 | 229.506 | 1.2596 | 285.983 | 1.2967 | 425.784 | 0.8939 | 501.163 | 1.05 | 676.499 | 1.0723
42.1795 | 6.6051 | 67.0832 | 3.6982 | 89.4727 | 2.5417 | 141.448 | 1.6617 | 213.99 | 1.4635 | 266.382 | 1.5096 | 398.191 | 1.0375 | 469.623 | 1.197 | 635.194 | 1.2273
40.1625 | 7.6894 | 63.3664 | 4.3225 | 84.8541 | 2.8917 | 134.549 | 1.8568 | 202.539 | 1.6534 | 251.12 | 1.7157 | 377.259 | 1.1686 | 446.72 | 1.3282 | 591.068 | 1.4331
38.3953 | 8.8008 | 60.0954 | 5.007 | 81.2015 | 3.2474 | 127.094 | 2.1209 | 190.363 | 1.8981 | 234.377 | 1.9994 | 359.219 | 1.3006 | 426.21 | 1.4708 | 554.979 | 1.6452
36.9636 | 10.1334 | 56.8794 | 5.8817 | 77.3959 | 3.6871 | 120.413 | 2.4178 | 178.919 | 2.1746 | 220.949 | 2.2998 | 338.977 | 1.4871 | 404.209 | 1.6567 | 525.28 | 1.8605
35.7637 | 11.703 | 54.1595 | 6.916 | 74.4356 | 4.1158 | 115.23 | 2.6989 | 166.489 | 2.5853 | 208.916 | 2.6244 | 323.09 | 1.6617 | 382.195 | 1.8886 | 501.664 | 2.0789
34.3958 | 14.3083 | 51.7764 | 8.1242 | 71.3027 | 4.636 | 109.501 | 3.0736 | 158.528 | 2.9033 | 199.723 | 2.9442 | 304.884 | 1.9038 | 363.192 | 2.1358 | 479.59 | 2.2998
33.3459 | 17.5814 | 49.6468 | 9.5338 | 68.7127 | 5.2218 | 104.369 | 3.4863 | 149.445 | 3.3529 | 188.846 | 3.407 | 293.222 | 2.0893 | 347.21 | 2.3889 | 453.018 | 2.6402
32.4251 | 21.7333 | 47.8434 | 11.188 | 66.6819 | 5.8348 | 100.076 | 3.9073 | 141.024 | 3.9034 | 179.995 | 3.8568 | 282.007 | 2.2975 | 329.947 | 2.7097 | 428.346 | 3.0187
31.8467 | 25.9156 | 46.2904 | 13.2479 | 64.1956 | 6.7927 | 95.6728 | 4.4497 | 135.494 | 4.3747 | 172.592 | 4.3486 | 273.125 | 2.5039 | 312.915 | 3.12 | 405.829 | 3.431
31.2161 | 32.5522 | 45.1475 | 15.4536 | 61.9876 | 7.8605 | 92.0134 | 5.002 | 131.096 | 4.7963 | 166.656 | 4.83 | 261.368 | 2.7839 | 298.847 | 3.539 | 387.196 | 3.8878
30.7514 | 39.2459 | 43.9888 | 18.5384 | 59.7359 | 9.2613 | 88.5824 | 5.6173 | 126.082 | 5.3273 | 162.054 | 5.2743 | 253.39 | 3.0278 | 284.841 | 4.0505 | 372.014 | 4.3269
30.4149 | 48.3684 | 43.2473 | 21.5817 | 57.7968 | 10.8465 | 85.5357 | 6.3334 | 121.38 | 5.9171 | 156.012 | 5.9289 | 243.942 | 3.3529 | 272.035 | 4.6779 | 357.785 | 4.8396
30.2028 | 60.0302 | 42.7314 | 25.2252 | 56.4262 | 12.3894 | 82.7591 | 7.1124 | 116.621 | 6.7251 | 150.947 | 6.6316 | 234.846 | 3.7279 | 261.892 | 5.2427 | 343.756 | 5.4349
30.0822 | 78.9527 | 42.1373 | 29.6317 | 55.0881 | 14.3944 | 80.3132 | 8.0112 | 112.385 | 7.6741 | 147.073 | 7.3437 | 227.223 | 4.0994 | 253.137 | 5.8935 | 330.938 | 6.0548
30.0221 | 108.185 | 41.6764 | 34.669 | 54.0513 | 16.7407 | 78.0956 | 9.0961 | 108.954 | 8.6438 | 142.726 | 8.2966 | 218.969 | 4.599 | 243.455 | 6.7318 | 319.875 | 6.7116
29.9921 | 153.216 | 41.2204 | 40.8476 | 53.2466 | 19.3336 | 76.3199 | 10.3072 | 105.312 | 10.1436 | 138.093 | 9.4013 | 212.073 | 5.0827 | 236.023 | 7.6358 | 307.333 | 7.5825
29.9921 | 221.152 | 40.8511 | 48.4653 | 52.4539 | 23.1929 | 74.2126 | 12.0112 | 102.098 | 11.7852 | 134.415 | 10.7708 | 205.805 | 5.6116 | 228.59 | 8.8715 | 298.847 | 8.4304
30.0221 | 317.301 | 40.5256 | 58.6066 | 51.7764 | 27.5732 | 72.4527 | 13.9411 | 99.279 | 13.6105 | 130.834 | 12.3646 | 199.923 | 6.1771 | 222.056 | 10.1334 | 290.886 | 9.4013
29.9921 | 467.712 | 40.3638 | 72.4465 | 51.21 | 33.3096 | 70.8761 | 15.9721 | 96.8278 | 15.9402 | 127.859 | 14.166 | 193.046 | 7.0487 | 217.659 | 11.4026 | 285.126 | 10.2763
29.9621 | 545.582 | 40.1625 | 91.5467 | 50.7004 | 40.0387 | 69.8908 | 18.0445 | 95.1004 | 18.2441 | 124.578 | 16.6739 | 186.22 | 8.0353 | 212.498 | 12.895 | 277.253 | 11.7499
29.9322 | 601.155 | 40.0422 | 121.492 | 50.3467 | 49.2962 | 68.5754 | 21.2604 | 93.2173 | 21.3456 | 121.867 | 19.3529 | 180.536 | 9.16 | 208.916 | 14.4377 | 271.763 | 13.103
|  | 40.0422 | 157.095 | 50.1959 | 62.4177 | 67.4195 | 24.7505 | 91.3715 | 25.0493 | 118.502 | 23.4729 | 174.85 | 10.5575 | 205.189 | 16.1488 | 265.584 | 14.7294
|  | 40.0823 | 198.115 | 50.1959 | 81.8468 | 66.5487 | 28.987 | 89.6518 | 29.1031 | 116.388 | 27.7947 | 170.193 | 12.0594 | 201.73 | 18.1169 | 259.545 | 16.8078
|  | 40.1224 | 273.924 | 50.1458 | 111.035 | 65.5579 | 34.3241 | 88.5824 | 33.5436 | 114.198 | 32.9452 | 165.659 | 14.294 | 196.946 | 21.2816 | 254.406 | 19.0077
|  | 40.1625 | 357.041 | 50.1458 | 143.861 | 64.7112 | 41.2994 | 87.1764 | 39.839 | 112.497 | 38.7003 | 162.216 | 16.5576 | 193.82 | 24.7257 | 248.621 | 21.9737
|  | 40.0823 | 437.402 | 50.1959 | 187.889 | 64.0033 | 50.2418 | 86.0505 | 46.7516 | 111.044 | 45.5972 | 158.686 | 19.2179 | 190.363 | 29.425 | 242.483 | 26.0195
|  | 40.0422 | 541.776 | 50.1959 | 253.623 | 63.2398 | 61.2429 | 84.939 | 56.0278 | 109.501 | 55.4703 | 154.768 | 23.2161 | 186.407 | 36.12 | 238.395 | 29.6614
|  | 40.0022 | 609.021 | 50.1959 | 345.451 | 62.7359 | 73.8362 | 84.2622 | 65.8809 | 108.303 | 65.6835 | 152.312 | 27.6561 | 182.898 | 43.9849 | 234.377 | 34.669
|  |  |  | 50.1959 | 466.777 | 62.1117 | 90.8173 | 83.5073 | 77.2347 | 106.904 | 81.765 | 149.744 | 33.1766 | 179.815 | 53.9926 | 230.657 | 39.2459
|  |  |  | 50.1959 | 566.713 | 61.6784 | 113.618 | 82.8419 | 91.9136 | 105.629 | 103.115 | 147.663 | 39.9587 | 177.493 | 63.4244 | 227.223 | 45.3245
|  |  |  | 50.1458 | 609.631 | 61.3094 | 140.59 | 82.3463 | 108.619 | 104.682 | 126.703 | 145.901 | 47.0329 | 175.376 | 74.2063 | 223.84 | 54.4263
[6 empty] | 60.9427 | 180.161 | 81.9356 | 131.479 | 103.227 | 167.981 | 144.161 | 56.3086 | 173.457 | 87.0819 | 220.949 | 63.5514
[6 empty] | 60.6994 | 228.343 | 81.6085 | 152.91 | 102.507 | 204.967 | 142.299 | 67.6839 | 171.217 | 102.498 | 217.877 | 76.3134
[6 empty] | 60.4571 | 295.258 | 80.7965 | 188.077 | 101.996 | 254.895 | 140.742 | 80.3064 | 169.853 | 118.019 | 214.848 | 91.5467
[6 empty] | 60.276 | 365.348 | 80.5545 | 239.092 | 101.487 | 314.144 | 138.508 | 102.909 | 168.331 | 136.982 | 211.649 | 113.732
[6 empty] | 60.2158 | 452.077 | 80.1527 | 309.777 | 101.082 | 384.849 | 136.719 | 130.562 | 166.989 | 161.233 | 208.916 | 135.89
[6 empty] | 60.0354 | 540.153 | 79.9926 | 416.069 | 100.477 | 487.287 | 134.819 | 168.823 | 165.328 | 191.684 | 206.63 | 161.717
[6 empty] | 60.0954 | 598.755 | 80.0726 | 527.872 | 100.276 | 570.124 | 133.477 | 205.583 | 164.011 | 226.75 | 204.165 | 196.537
[8 empty] | 80.0726 | 573.555 | 100.076 | 602.359 | 132.281 | 269.037 | 162.704 | 269.037 | 202.134 | 237.187
[8 empty] | 80.0726 | 598.157 |  |  | 131.358 | 324.359 | 161.892 | 311.329 | 200.523 | 280.858
[12 empty] | 130.573 | 405.797 | 160.924 | 371.984 | 198.926 | 330.581
[12 empty] | 130.051 | 501.625 | 159.961 | 451.625 | 197.341 | 414.408
[12 empty] | 129.662 | 572.409 | 159.322 | 532.111 | 196.356 | 496.634
[12 empty] | 129.662 | 602.359 | 158.686 | 573.555 | 196.16 | 566.713
[14 empty] | 158.211 | 602.359 | 195.768 | 593.391