## 153_151
S&C Power Fuses - Type SMD-1A (34.5 and 46 kV) | [9 empty] | S&C Power Fuses - Type SMD-1A (34.5 and 46 kV) | [9 empty] | S&C Power Fuses - Type SMD-1A (34.5 and 46 kV) | [9 empty] | S&C Power Fuses - Type SMD-1A (34.5 and 46 kV)
Standard Speed (TCC 153-1-5-1) | [9 empty] | Standard Speed (TCC 153-1-5-1) | [9 empty] | Standard Speed (TCC 153-1-5-1) | [9 empty] | Standard Speed (TCC 153-1-5-1)
Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
3E |  | 5E |  | 7E |  | 10E |  | 13E |  | 15E |  | 20E |  | 25E |  | 30E |  | 40E |  | 50E |  | 65E |  | 80E |  | 100E |  | 125E |  | 150E |  | 175E |  | 200E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
23502.3 | 0.015903 | 23502.3 | 0.015903 | 23502.3 | 0.015903 | 23502.3 | 0.015903 | 23502.3 | 0.015903 | 23502.3 | 0.015903 | 23502.3 | 0.015903 | 23502.3 | 0.015903 | 23502.3 | 0.015998 | 23502.3 | 0.015998 | 23502.3 | 0.015998 | 23502.3 | 0.016093 | 23502.3 | 0.016302 | 23502.3 | 0.0164 | 23430.3 | 0.016845 | 23309.8 | 0.017324 | 23323.2 | 0.017858 | 23296.4 | 0.018418
21935.2 | 0.016498 | 21223.1 | 0.016796 | 21350.9 | 0.016796 | 23431.9 | 0.015903 | 22177.8 | 0.0164 | 22266.7 | 0.0164 | 22580.7 | 0.016302 | 22899.1 | 0.016206 | 23059.9 | 0.016093 | 22089.3 | 0.016597 | 22535.6 | 0.0164 | 23455.3 | 0.016093 | 22944.9 | 0.016498 | 22580.7 | 0.016796 | 21279.6 | 0.017797 | 21230.9 | 0.018376 | 19193.8 | 0.020301 | 19785.7 | 0.020488
20370.5 | 0.017201 | 19729 | 0.017494 | 19867.6 | 0.017407 | 22001.1 | 0.016498 | 20740.5 | 0.017099 | 20844.5 | 0.016997 | 21159.6 | 0.016896 | 21479.4 | 0.016796 | 21630.2 | 0.016696 | 20657.7 | 0.017201 | 21096.2 | 0.016997 | 22045.2 | 0.016696 | 21522.4 | 0.017099 | 21159.6 | 0.017494 | 18000.5 | 0.020024 | 18114.3 | 0.020676 | 15217.9 | 0.024077 | 15122.3 | 0.024932
18804.3 | 0.018005 | 18230.3 | 0.018293 | 18376.7 | 0.018203 | 20575.3 | 0.017099 | 19319 | 0.017703 | 19415.8 | 0.017703 | 19729 | 0.017494 | 20047.2 | 0.017407 | 20188 | 0.017407 | 19222.6 | 0.017898 | 19669.9 | 0.017703 | 20595.9 | 0.017407 | 20087.3 | 0.017792 | 19729 | 0.018293 | 14745.7 | 0.022855 | 15191.8 | 0.023437 | 12755.4 | 0.027464 | 12267.8 | 0.029417
17254.6 | 0.018791 | 16744.7 | 0.019092 | 16879.2 | 0.018997 | 19145.9 | 0.017792 | 17887.2 | 0.018494 | 17976.8 | 0.018403 | 18303.3 | 0.018293 | 18617.2 | 0.018095 | 18766.7 | 0.018095 | 17797.9 | 0.018605 | 18248.5 | 0.018403 | 19184.2 | 0.018095 | 18654.5 | 0.018605 | 18285.1 | 0.019092 | 12296 | 0.025729 | 12051.8 | 0.027527 | 10666.8 | 0.031563 | 9430.24 | 0.036733
15690.8 | 0.019708 | 15242.3 | 0.020004 | 15380.1 | 0.019905 | 17709.2 | 0.018494 | 16445.9 | 0.019301 | 16561.5 | 0.019206 | 16862.3 | 0.019092 | 17185.8 | 0.018903 | 17341.1 | 0.018791 | 16363.9 | 0.019494 | 16811.8 | 0.019301 | 17744.6 | 0.018903 | 17237.4 | 0.019398 | 16862.3 | 0.020004 | 9610.29 | 0.030202 | 9715.51 | 0.032313 | 8869.32 | 0.036712 | 7602.13 | 0.04532
14126.8 | 0.020794 | 13750.4 | 0.021107 | 13888.6 | 0.021002 | 16282.3 | 0.019398 | 15015.4 | 0.020204 | 15120.8 | 0.020104 | 15441.8 | 0.019905 | 15753.7 | 0.019806 | 15912 | 0.019708 | 14940.5 | 0.020406 | 15380.1 | 0.020204 | 16314.9 | 0.019806 | 15801 | 0.020406 | 15426.3 | 0.021107 | 7602.13 | 0.035799 | 7729.54 | 0.0393 | 7113.16 | 0.045087 | 6184.87 | 0.056851
12579.4 | 0.022006 | 12256.6 | 0.022292 | 12392.2 | 0.022203 | 14851.1 | 0.020305 | 13586.4 | 0.021191 | 13695.5 | 0.021107 | 14000.2 | 0.020898 | 14325.9 | 0.020794 | 14484.4 | 0.020691 | 13505.1 | 0.021509 | 13958.2 | 0.021191 | 14880.8 | 0.020794 | 14369 | 0.021509 | 14000.2 | 0.022403 | 6375.62 | 0.041283 | 6135.44 | 0.049214 | 5793.7 | 0.055979 | 4943.22 | 0.075257
11012.8 | 0.023404 | 10762.4 | 0.023708 | 10892.3 | 0.02359 | 13424.3 | 0.021296 | 12158.9 | 0.022403 | 12268.8 | 0.022292 | 12579.4 | 0.022093 | 12897.9 | 0.021897 | 13053.6 | 0.02181 | 12074.1 | 0.022694 | 12529.2 | 0.022403 | 13451.2 | 0.021897 | 12936.7 | 0.022807 | 12566.9 | 0.023897 | 5213.84 | 0.049214 | 4946.05 | 0.061948 | 4800.82 | 0.07002 | 4056.38 | 0.099509
9450.37 | 0.025089 | 9272.5 | 0.025289 | 9403.23 | 0.025189 | 12001.9 | 0.022492 | 10730.1 | 0.023802 | 10838 | 0.023708 | 11145.7 | 0.023404 | 11462.3 | 0.023103 | 11612.2 | 0.022989 | 10644.6 | 0.024208 | 11101.2 | 0.023897 | 12025.9 | 0.023311 | 11508.2 | 0.024401 | 11145.7 | 0.025694 | 4385.2 | 0.058568 | 3935.02 | 0.081303 | 4010.15 | 0.08839 | 3319.12 | 0.13416
7893.54 | 0.027191 | 7776.01 | 0.027408 | 7901.44 | 0.027191 | 10570.4 | 0.023897 | 9300.36 | 0.025289 | 9403.23 | 0.025189 | 9718.73 | 0.02489 | 10034.7 | 0.024693 | 10186.4 | 0.024498 | 9217.02 | 0.025899 | 9670.25 | 0.025491 | 10591.5 | 0.02489 | 10085 | 0.026288 | 9709.02 | 0.027902 | 3700.96 | 0.070624 | 3249.47 | 0.10489 | 3232.76 | 0.12075 | 2664.97 | 0.19066
6334.64 | 0.029704 | 6277.88 | 0.029912 | 6411.12 | 0.029587 | 9134.44 | 0.025491 | 7869.89 | 0.027299 | 7972.87 | 0.02711 | 8289.98 | 0.026789 | 8611.07 | 0.026498 | 8758.72 | 0.026288 | 7783.79 | 0.028014 | 8240.38 | 0.027599 | 9161.89 | 0.026896 | 8654.24 | 0.028604 | 8281.69 | 0.030908 | 3012.71 | 0.091269 | 2547 | 0.14983 | 2570.47 | 0.17289 | 2155.75 | 0.27174
4773.21 | 0.0332 | 4782.77 | 0.0332 | 4913.67 | 0.032905 | 7706.34 | 0.02749 | 6443.26 | 0.029704 | 6547.19 | 0.029499 | 6855.41 | 0.029091 | 7178.14 | 0.028689 | 7330.48 | 0.028491 | 6353.68 | 0.030786 | 6807.58 | 0.0303 | 7737.23 | 0.029411 | 7221.34 | 0.031812 | 6848.55 | 0.035099 | 2558.71 | 0.1141 | 2006.72 | 0.21699 | 2052.07 | 0.25024 | 1733.87 | 0.39716
3215.55 | 0.038116 | 3287.08 | 0.037889 | 3417.82 | 0.037515 | 6277.88 | 0.029912 | 5012.94 | 0.032807 | 5114.21 | 0.032612 | 5425.04 | 0.032002 | 5749.02 | 0.031591 | 5900.46 | 0.03131 | 4923.51 | 0.034511 | 5376.43 | 0.0339 | 6303.05 | 0.032807 | 5795.19 | 0.036486 | 5419.62 | 0.041598 | 2210.81 | 0.14077 | 1637.29 | 0.304 | 1665.68 | 0.35972 | 1386.58 | 0.60386
1655.27 | 0.046308 | 1793.14 | 0.045578 | 1925.09 | 0.044993 | 4845.35 | 0.033101 | 3582.3 | 0.037107 | 3687.71 | 0.036887 | 3998.86 | 0.036197 | 4318.96 | 0.035485 | 4468.34 | 0.035309 | 3493.85 | 0.040497 | 3947.21 | 0.039582 | 4874.51 | 0.037889 | 4362.37 | 0.044284 | 5338.93 | 0.04218 | 1845.64 | 0.18528 | 1355.15 | 0.42418 | 1318.38 | 0.55672 | 1092.45 | 0.98286
95.067 | 0.077009 | 299.058 | 0.073132 | 429.944 | 0.070493 | 3417.82 | 0.037589 | 2151.1 | 0.044196 | 2256.88 | 0.043803 | 2567.64 | 0.042813 | 2889.24 | 0.042013 | 3037.38 | 0.041598 | 2064.68 | 0.053589 | 2516.8 | 0.051094 | 3445.27 | 0.047191 | 4306.02 | 0.044682 | 5201.9 | 0.042984 | 1548.75 | 0.24612 | 1151.59 | 0.57027 | 1071.36 | 0.82164 | 885.227 | 1.5617
92.9054 | 0.077469 | 294.311 | 0.073569 | 420.168 | 0.071197 | 1987.69 | 0.044904 | 721.752 | 0.065692 | 826.078 | 0.064272 | 1137.63 | 0.060674 | 1457.84 | 0.057791 | 1607.96 | 0.056711 | 2033.94 | 0.054124 | 2486.77 | 0.051604 | 3397.37 | 0.047709 | 4178.75 | 0.045714 | 5028 | 0.044196 | 1274.54 | 0.34029 | 970.239 | 0.79663 | 892.358 | 1.2126 | 746.673 | 2.558
88.9949 | 0.078398 | 284.472 | 0.074599 | 403.289 | 0.072409 | 558.173 | 0.06822 | 711.718 | 0.066085 | 813.778 | 0.064721 | 1110.65 | 0.061524 | 1424.69 | 0.058484 | 1579.27 | 0.057277 | 1977.78 | 0.054991 | 2427.8 | 0.052379 | 3277.24 | 0.048812 | 3896.23 | 0.048281 | 4787.55 | 0.045988 | 1120.34 | 0.42809 | 854.324 | 1.0319 | 765.303 | 1.7794 | 661.246 | 3.9793
83.8959 | 0.079892 | 274.962 | 0.075569 | 381.324 | 0.074082 | 544.936 | 0.068832 | 685.179 | 0.067211 | 787.361 | 0.065823 | 1075.67 | 0.062571 | 1344.41 | 0.060493 | 1535.66 | 0.058195 | 1896.43 | 0.056374 | 2351.34 | 0.053483 | 3161.35 | 0.050188 | 3582.3 | 0.051604 | 4554.05 | 0.047899 | 959.181 | 0.56281 | 711.986 | 1.5431 | 652.961 | 2.8162 | 591.665 | 6.1834
79.406 | 0.081333 | 263.126 | 0.076932 | 360.196 | 0.076096 | 526.718 | 0.069865 | 664.927 | 0.068287 | 755.73 | 0.067211 | 1041.79 | 0.063574 | 1266.11 | 0.062821 | 1476.92 | 0.05948 | 1812.98 | 0.058195 | 2265.92 | 0.054773 | 3037.38 | 0.051604 | 3326.77 | 0.054773 | 4166.23 | 0.051809 | 840.242 | 0.72318 | 622.628 | 2.1384 | 562.243 | 4.6444 | 541.993 | 10.645
74.1856 | 0.083213 | 247.554 | 0.079024 | 336.179 | 0.07871 | 508.601 | 0.070985 | 641.415 | 0.069519 | 719.59 | 0.068969 | 997.945 | 0.065172 | 1158.29 | 0.066282 | 1404.89 | 0.061402 | 1714.24 | 0.060373 | 2181.43 | 0.056318 | 2924.12 | 0.053218 | 3064.84 | 0.05901 | 3888.44 | 0.05521 | 700.652 | 1.0443 | 545.109 | 3.2014 | 505.391 | 7.5162 | 509.171 | 19.6401
68.6874 | 0.0859 | 235.244 | 0.08093 | 299.058 | 0.083793 | 491.107 | 0.072194 | 612.576 | 0.071126 | 674.302 | 0.07148 | 944.538 | 0.067277 | 1077.82 | 0.069588 | 1316.47 | 0.06389 | 1598.34 | 0.063385 | 2081.27 | 0.058195 | 2710.11 | 0.056318 | 2795.45 | 0.064209 | 3585.88 | 0.059599 | 583.917 | 1.5475 | 486.632 | 5.0724 | 461.902 | 14.5172 | 491.678 | 38.3927
64.1076 | 0.088675 | 219.34 | 0.083627 | 268.441 | 0.089471 | 452.442 | 0.07512 | 580.373 | 0.073205 | 616.263 | 0.075269 | 894.883 | 0.069588 | 987.027 | 0.073935 | 1232.38 | 0.066811 | 1427.55 | 0.068901 | 1958.1 | 0.060795 | 2524.36 | 0.059717 | 2601.24 | 0.068696 | 3336.76 | 0.064017 | 504.812 | 2.2005 | 451.952 | 7.6991 | 442.469 | 27.2016 | 489.148 | 70.0284
59.2377 | 0.092086 | 205.125 | 0.0865 | 237.371 | 0.097354 | 418.072 | 0.078476 | 549.313 | 0.075494 | 572.877 | 0.078867 | 841.924 | 0.072265 | 912.049 | 0.078476 | 1145.62 | 0.070423 | 1303.37 | 0.07423 | 1853.31 | 0.063322 | 2337.27 | 0.0637 | 2442.41 | 0.073423 | 3016.2 | 0.071267 | 432.688 | 3.4389 | 423.367 | 13.361 | 436.424 | 50.7068 | 486.074 | 136.423
53.6003 | 0.097354 | 190.302 | 0.090275 | 212.219 | 0.10614 | 385.928 | 0.082064 | 507.078 | 0.079181 | 535.75 | 0.082636 | 784.217 | 0.075794 | 845.299 | 0.083378 | 1058.59 | 0.074599 | 1198.35 | 0.079575 | 1733.2 | 0.066811 | 2106.39 | 0.069796 | 2290.99 | 0.078476 | 2759.34 | 0.07871 | 391.846 | 4.9718 | 411.171 | 19.4499 | 428.739 | 103.826 | 483.851 | 240.159
48.84 | 0.10354 | 176.375 | 0.094683 | 187.282 | 0.11804 | 351.302 | 0.087103 | 471.378 | 0.082965 | 492.583 | 0.087624 | 728.278 | 0.079971 | 779.526 | 0.089471 | 988.015 | 0.07871 | 1110.65 | 0.08539 | 1645.37 | 0.069796 | 1927.02 | 0.076096 | 2136.09 | 0.084714 | 2469.43 | 0.089382 | 361.219 | 7.4862 | 399.327 | 27.2327 | 424.096 | 209.692 | 483.019 | 410.144
45.2203 | 0.10935 | 160.711 | 0.101 | 170.138 | 0.1296 | 317.869 | 0.093283 | 439.948 | 0.087017 | 447.044 | 0.094401 | 674.302 | 0.084798 | 708.168 | 0.097936 | 904.781 | 0.084798 | 1019.12 | 0.092821 | 1532.59 | 0.074082 | 1729.73 | 0.084967 | 1963.98 | 0.093283 | 2272.73 | 0.099307 | 338.179 | 11.8003 | 388.269 | 42.5594 | 424.582 | 333.766 | 481.637 | 559.98
41.5767 | 0.11723 | 147.467 | 0.10763 | 151.806 | 0.14615 | 289.06 | 0.1005 | 398.478 | 0.093468 | 398.877 | 0.10416 | 634.397 | 0.089205 | 655.683 | 0.1053 | 830.219 | 0.091721 | 932.337 | 0.1017 | 1460.76 | 0.077469 | 1558.87 | 0.095344 | 1794.94 | 0.10385 | 2046.18 | 0.11356 | 321.547 | 20.303 | 380.34 | 69.3502 | 425.556 | 495.136 | 480.534 | 592.969
37.62 | 0.12806 | 130.398 | 0.1197 | 139.296 | 0.16125 | 263.916 | 0.10838 | 365.639 | 0.1003 | 353.77 | 0.11641 | 595.661 | 0.093934 | 605.875 | 0.11435 | 753.466 | 0.1006 | 856.36 | 0.11155 | 1390.91 | 0.081172 | 1427.55 | 0.10562 | 1670.24 | 0.11378 | 1879.44 | 0.12743 | 313.001 | 32.5018 | 372.573 | 119.937 | 424.582 | 593.309 | 480.534 | 592.969
34.6928 | 0.13879 | 115.884 | 0.13392 | 123.42 | 0.18791 | 240.718 | 0.11781 | 330.512 | 0.10968 | 315.337 | 0.13141 | 551.515 | 0.1004 | 540.593 | 0.12998 | 686.55 | 0.11099 | 778.747 | 0.12455 | 1321.75 | 0.085305 | 1308.59 | 0.11793 | 1565.12 | 0.12393 | 1719.39 | 0.14456 | 307.489 | 61.2495 | 367.484 | 217.392 | 424.582 | 593.309 | 480.534 | 592.969
31.8019 | 0.15238 | 103.294 | 0.15117 | 108.591 | 0.22292 | 219.779 | 0.12896 | 296.082 | 0.12198 | 283.053 | 0.14834 | 497.036 | 0.11099 | 494.063 | 0.14514 | 641.415 | 0.11958 | 712.43 | 0.13865 | 1239.8 | 0.090904 | 1195.96 | 0.13246 | 1424.69 | 0.14074 | 1577.69 | 0.16416 | 303.636 | 119.594 | 363.712 | 371.687 | 424.582 | 593.309 | 480.534 | 592.969
28.8331 | 0.17082 | 92.627 | 0.17133 | 97.8645 | 0.25925 | 201.465 | 0.14144 | 268.173 | 0.13552 | 251.295 | 0.17133 | 460.199 | 0.12017 | 453.801 | 0.16109 | 599.846 | 0.12908 | 642.056 | 0.15887 | 1180.51 | 0.095723 | 1093.02 | 0.14997 | 1315.15 | 0.15761 | 1424.69 | 0.19187 | 300.348 | 206.476 | 361.634 | 524.305 | 424.582 | 593.309 | 480.534 | 592.969
26.8837 | 0.18716 | 83.6445 | 0.19456 | 88.1093 | 0.30451 | 185.975 | 0.15497 | 245.581 | 0.14968 | 230.356 | 0.19244 | 416.82 | 0.13445 | 421.009 | 0.17827 | 547.667 | 0.14427 | 583.282 | 0.18149 | 1117.33 | 0.1016 | 952.125 | 0.18203 | 1211.61 | 0.17686 | 1300.77 | 0.22181 | 297.948 | 352.217 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
24.5943 | 0.21127 | 72.2093 | 0.23802 | 78.9309 | 0.36269 | 171.848 | 0.17014 | 226.02 | 0.16514 | 211.372 | 0.21723 | 384.387 | 0.14775 | 390.587 | 0.19767 | 512.687 | 0.15683 | 533.611 | 0.2063 | 1049.11 | 0.10946 | 867.566 | 0.20981 | 1097.4 | 0.20507 | 1198.35 | 0.2544 | 295.905 | 534.303 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
22.6127 | 0.23897 | 61.9645 | 0.29912 | 70.0751 | 0.44196 | 156.743 | 0.19168 | 206.979 | 0.18494 | 195.511 | 0.24304 | 352.71 | 0.16432 | 354.478 | 0.22717 | 473.268 | 0.17476 | 485.249 | 0.23731 | 990.983 | 0.11699 | 791.307 | 0.24256 | 977.206 | 0.2462 | 1128.56 | 0.28153 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
20.3994 | 0.27958 | 55.2327 | 0.35875 | 62.9639 | 0.53059 | 145.707 | 0.2117 | 188.597 | 0.21044 | 173.228 | 0.29149 | 323.967 | 0.18385 | 333.5 | 0.2494 | 436.879 | 0.19533 | 442.154 | 0.27435 | 902.071 | 0.13115 | 729.006 | 0.27682 | 885.978 | 0.28918 | 1064.96 | 0.31217 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
18.8121 | 0.31938 | 50.2269 | 0.41888 | 55.5096 | 0.66282 | 134.639 | 0.23684 | 168.108 | 0.24816 | 153.332 | 0.35555 | 297.269 | 0.20691 | 310.642 | 0.27764 | 404.5 | 0.2181 | 389.807 | 0.33698 | 840.242 | 0.14356 | 680.399 | 0.31001 | 795.274 | 0.3458 | 1004.95 | 0.34683 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
17.6634 | 0.35697 | 46.2724 | 0.48042 | 50.1265 | 0.79733 | 123.915 | 0.26683 | 150.145 | 0.29469 | 140.274 | 0.41146 | 273.591 | 0.23288 | 286.184 | 0.31529 | 374.521 | 0.24498 | 362.726 | 0.38154 | 788.148 | 0.15636 | 641.415 | 0.34272 | 727.55 | 0.40136 | 952.125 | 0.38458 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
16.6348 | 0.39858 | 43.2736 | 0.54017 | 45.2203 | 0.95914 | 115.537 | 0.29704 | 138.739 | 0.33299 | 127.179 | 0.4886 | 245.827 | 0.27326 | 261.813 | 0.3645 | 350.951 | 0.27137 | 337.189 | 0.43112 | 725.37 | 0.17563 | 596.854 | 0.38765 | 685.864 | 0.44549 | 880.678 | 0.44416 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
15.666 | 0.44904 | 40.835 | 0.59717 | 41.9946 | 1.1055 | 106.76 | 0.33531 | 130.138 | 0.3685 | 119.892 | 0.53856 | 217.81 | 0.32937 | 241.441 | 0.41722 | 323.643 | 0.30817 | 320.423 | 0.47285 | 666.925 | 0.19846 | 561.532 | 0.42899 | 649.808 | 0.48618 | 831.881 | 0.49495 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
14.7979 | 0.50438 | 38.5339 | 0.66019 | 39.4699 | 1.243 | 98.7493 | 0.3804 | 123.173 | 0.40176 | 112.91 | 0.59303 | 197.871 | 0.38611 | 212.432 | 0.51758 | 302.971 | 0.34375 | 305.405 | 0.51502 | 577.478 | 0.24669 | 530.949 | 0.47191 | 616.263 | 0.53589 | 784.217 | 0.55706 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
14.2035 | 0.55265 | 35.8568 | 0.75195 | 37.3202 | 1.3921 | 90.6114 | 0.43846 | 116.932 | 0.43846 | 106.653 | 0.65692 | 175.671 | 0.47238 | 192.215 | 0.61769 | 274.138 | 0.40658 | 294.017 | 0.5532 | 504.044 | 0.30725 | 509.11 | 0.50992 | 587.38 | 0.58601 | 740.024 | 0.62571 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
13.4972 | 0.622 | 33.466 | 0.8522 | 35.9645 | 1.4997 | 83.4774 | 0.50338 | 111.006 | 0.47994 | 98.3551 | 0.7587 | 157.056 | 0.57562 | 175.495 | 0.72481 | 253.567 | 0.46585 | 278.004 | 0.61219 | 456.989 | 0.36125 | 489.636 | 0.54991 | 551.515 | 0.66019 | 701.823 | 0.69658 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
12.7877 | 0.70914 | 31.6433 | 0.94589 | 34.4852 | 1.6351 | 78.5372 | 0.56095 | 104.646 | 0.53007 | 92.7197 | 0.84883 | 143.251 | 0.6768 | 161.516 | 0.84044 | 231.048 | 0.54719 | 267.102 | 0.66151 | 409.384 | 0.43716 | 470.436 | 0.59068 | 520.956 | 0.73789 | 669.598 | 0.7678 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
11.9709 | 0.83544 | 29.6518 | 1.0667 | 33.2325 | 1.7668 | 74.7815 | 0.61524 | 99.5425 | 0.57791 | 85.9338 | 0.97741 | 129.101 | 0.82064 | 150.747 | 0.95439 | 211.372 | 0.6389 | 257.657 | 0.70914 | 381.706 | 0.49545 | 440.388 | 0.67011 | 490.126 | 0.83461 | 626.203 | 0.88587 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
11.3984 | 0.95818 | 27.2355 | 1.2492 | 31.9614 | 1.9302 | 69.7256 | 0.69588 | 93.7453 | 0.644 | 81.9882 | 1.0731 | 120.132 | 0.93934 | 140.836 | 1.0913 | 188.597 | 0.7871 | 246.812 | 0.77085 | 361.278 | 0.54448 | 417.655 | 0.74599 | 461.121 | 0.94495 | 597.451 | 0.9813 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
10.9077 | 1.0924 | 25.3941 | 1.4285 | 30.862 | 2.0836 | 65.7963 | 0.77546 | 86.2783 | 0.74822 | 77.5228 | 1.1982 | 112.797 | 1.0614 | 131.314 | 1.248 | 173.401 | 0.92913 | 234.54 | 0.85305 | 343.657 | 0.59599 | 389.417 | 0.86071 | 439.069 | 1.0457 | 561.532 | 1.13 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
10.4695 | 1.2455 | 23.8913 | 1.6029 | 29.7112 | 2.2671 | 62.3998 | 0.85305 | 79.8839 | 0.86157 | 73.3006 | 1.3405 | 106.228 | 1.1899 | 123.05 | 1.4214 | 163.794 | 1.0395 | 221.323 | 0.962 | 330.182 | 0.64336 | 367.472 | 0.97064 | 423.967 | 1.1322 | 530.419 | 1.2883 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
10.1094 | 1.3976 | 22.6806 | 1.7721 | 28.7754 | 2.4474 | 58.7657 | 0.96105 | 74.5575 | 0.98228 | 70.2154 | 1.4702 | 101.553 | 1.3063 | 116.815 | 1.5855 | 153.792 | 1.184 | 208.225 | 1.0946 | 314.078 | 0.70774 | 347.459 | 1.0913 | 407.75 | 1.2406 | 504.044 | 1.4543 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
9.8009 | 1.5605 | 21.6176 | 1.9513 | 27.6747 | 2.6736 | 56.1236 | 1.0561 | 69.8652 | 1.1143 | 66.724 | 1.6416 | 96.5039 | 1.4528 | 109.902 | 1.8167 | 145.271 | 1.3352 | 198.466 | 1.2137 | 297.864 | 0.78243 | 327.223 | 1.2406 | 394.908 | 1.3272 | 485.734 | 1.5871 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
9.3977 | 1.8149 | 20.7699 | 2.1233 | 26.5364 | 2.9616 | 53.7613 | 1.1538 | 65.5337 | 1.2642 | 63.3429 | 1.8458 | 92.9054 | 1.5698 | 104.646 | 2.0204 | 136.947 | 1.5207 | 190.302 | 1.3272 | 283.904 | 0.85986 | 310.021 | 1.4004 | 382.088 | 1.4299 | 472.322 | 1.7065 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
9.1291 | 2.0305 | 19.8758 | 2.3334 | 25.5214 | 3.2482 | 51.6532 | 1.2517 | 62.1506 | 1.4087 | 60.4345 | 2.0528 | 89.0839 | 1.7252 | 98.947 | 2.3012 | 130.66 | 1.6896 | 183.023 | 1.4586 | 268.71 | 0.95914 | 296.378 | 1.5482 | 367.105 | 1.5761 | 456.076 | 1.8772 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
8.8859 | 2.2898 | 19.1347 | 2.5415 | 24.6189 | 3.5591 | 49.6774 | 1.3593 | 58.8245 | 1.5808 | 57.7173 | 2.2966 | 85.5052 | 1.8884 | 93.2777 | 2.6393 | 124.411 | 1.8922 | 176.198 | 1.5918 | 256.629 | 1.053 | 282.205 | 1.7528 | 354.478 | 1.7218 | 439.509 | 2.0671 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
8.7099 | 2.544 | 18.366 | 2.7958 | 23.8435 | 3.8803 | 47.5864 | 1.4893 | 55.7878 | 1.7668 | 55.1775 | 2.5694 | 81.2536 | 2.1254 | 89.7995 | 2.8976 | 118.699 | 2.1296 | 170.82 | 1.7235 | 244.601 | 1.1618 | 270.598 | 1.9398 | 341.943 | 1.8828 | 421.009 | 2.3241 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
8.5034 | 2.9062 | 17.7342 | 3.0451 | 23.162 | 4.1888 | 45.0848 | 1.658 | 53.12 | 1.963 | 52.7494 | 2.8861 | 77.4453 | 2.3873 | 85.0787 | 3.32 | 113.023 | 2.4135 | 165.109 | 1.8735 | 232.671 | 1.2934 | 263.126 | 2.0898 | 330.512 | 2.0548 | 406.935 | 2.5567 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
8.3183 | 3.3068 | 17.1585 | 3.3003 | 22.0764 | 4.7947 | 43.2736 | 1.8239 | 50.4282 | 2.1962 | 50.8333 | 3.2066 | 73.8156 | 2.6736 | 80.6867 | 3.8344 | 108.049 | 2.7029 | 160.39 | 2.0084 | 223.547 | 1.4228 | 254.584 | 2.283 | 318.187 | 2.2762 | 393.725 | 2.8181 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
8.1292 | 3.8649 | 16.5352 | 3.6233 | 21.3811 | 5.2849 | 41.2042 | 2.0264 | 47.9207 | 2.4669 | 48.645 | 3.6486 | 70.992 | 2.9557 | 76.2923 | 4.4859 | 103.605 | 3.0391 | 155.183 | 2.2006 | 212.644 | 1.595 | 246.812 | 2.5064 | 304.795 | 2.5618 | 379.802 | 3.1248 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
8.0082 | 4.3672 | 15.9027 | 4.0096 | 20.7699 | 5.7849 | 39.3123 | 2.2514 | 45.3108 | 2.8125 | 46.9718 | 4.082 | 68.2765 | 3.2774 | 73.5945 | 5.0089 | 99.7418 | 3.3933 | 150.295 | 2.3968 | 204.51 | 1.7511 | 239.757 | 2.7272 | 295.786 | 2.8153 | 368.576 | 3.4341 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.8653 | 5.0238 | 15.3251 | 4.4372 | 20.2368 | 6.2758 | 37.7708 | 2.4669 | 43.534 | 3.1279 | 45.3561 | 4.5896 | 65.1416 | 3.7366 | 70.992 | 5.6039 | 96.1186 | 3.7965 | 144.691 | 2.6577 | 196.687 | 1.9263 | 231.51 | 3.009 | 284.188 | 3.1749 | 359.476 | 3.7515 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.7559 | 5.7849 | 14.9019 | 4.8042 | 19.6977 | 6.89 | 35.8927 | 2.7764 | 41.7852 | 3.458 | 43.7523 | 5.1912 | 62.901 | 4.1105 | 68.4817 | 6.3322 | 93.1845 | 4.2264 | 139.574 | 2.9675 | 189.732 | 2.1149 | 224.443 | 3.3101 | 277.448 | 3.4752 | 349.899 | 4.135 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.6405 | 6.6546 | 14.447 | 5.3007 | 19.2691 | 7.4525 | 34.6235 | 3.021 | 40.1065 | 3.8496 | 42.1208 | 5.9186 | 60.9199 | 4.5262 | 66.3248 | 7.1267 | 90.5208 | 4.7191 | 134.236 | 3.3399 | 181.565 | 2.3826 | 216.29 | 3.674 | 268.441 | 3.8919 | 343.314 | 4.4726 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.5342 | 7.5494 | 14.034 | 5.8368 | 18.8121 | 8.1901 | 33.4995 | 3.2709 | 38.4953 | 4.2898 | 40.7534 | 6.7011 | 58.7657 | 5.069 | 64.4934 | 7.9892 | 88.1093 | 5.2901 | 128.714 | 3.8078 | 173.401 | 2.7029 | 209.478 | 4.082 | 263.916 | 4.2474 | 336.179 | 4.8909 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.4444 | 8.6844 | 13.6465 | 6.4978 | 18.3843 | 8.9916 | 32.5419 | 3.5099 | 37.0228 | 4.7852 | 39.5094 | 7.5719 | 57.2002 | 5.5595 | 62.8381 | 8.9471 | 85.4197 | 6.0373 | 125.16 | 4.2264 | 166.103 | 3.0451 | 204.92 | 4.4372 | 257.657 | 4.7004 | 329.192 | 5.3696 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.3703 | 10.1501 | 13.4031 | 7.0074 | 18.0744 | 9.7935 | 31.454 | 3.8192 | 35.8927 | 5.2171 | 38.4953 | 8.4967 | 55.6207 | 6.1585 | 60.9199 | 10.2718 | 83.3106 | 6.8491 | 122.314 | 4.6216 | 160.069 | 3.4238 | 199.86 | 4.857 | 252.808 | 5.1655 | 322.029 | 5.9539 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.3042 | 12.1977 | 13.0721 | 7.77 | 17.752 | 10.6881 | 30.3721 | 4.2013 | 35.0415 | 5.5761 | 37.5073 | 9.5628 | 54.139 | 6.7612 | 59.5347 | 11.7109 | 80.7675 | 8.1738 | 119.652 | 5.1502 | 154.718 | 3.8154 | 195.511 | 5.3007 | 248.298 | 5.7562 | 316.6 | 6.5108 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.2388 | 14.644 | 12.7239 | 8.6586 | 17.4877 | 11.6182 | 29.3861 | 4.5987 | 34.1763 | 6.0194 | 36.6544 | 10.6352 | 52.8022 | 7.4525 | 58.6483 | 13.1935 | 78.6158 | 9.6967 | 117.166 | 5.7791 | 150.446 | 4.1597 | 191.065 | 5.901 | 243.137 | 6.4914 | 310.952 | 7.1693 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.1883 | 17.4937 | 12.447 | 9.6583 | 17.2791 | 12.7807 | 28.4322 | 5.074 | 33.3991 | 6.4978 | 36.0366 | 11.8161 | 51.6016 | 8.2227 | 57.5444 | 15.283 | 76.5215 | 11.7342 | 114.273 | 6.5823 | 147.467 | 4.4904 | 187.282 | 6.485 | 237.134 | 7.4525 | 304.795 | 7.9259 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.1382 | 21.2327 | 12.1883 | 10.8702 | 17.0559 | 14.1858 | 27.2627 | 5.7107 | 32.7378 | 6.9727 | 35.5 | 13.0631 | 50.681 | 9.0185 | 56.5178 | 18.1306 | 74.6321 | 14.214 | 112.571 | 7.3496 | 144.691 | 4.8281 | 183.39 | 7.2265 | 232.671 | 8.421 | 297.864 | 9.1176 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.1382 | 24.7916 | 11.9589 | 12.6042 | 16.8693 | 15.6985 | 26.5364 | 6.1953 | 31.9614 | 7.587 | 35.0064 | 15.0122 | 49.8267 | 9.9406 | 55.6207 | 22.1153 | 72.935 | 17.7739 | 110.012 | 8.573 | 142.252 | 5.2327 | 179.938 | 8.029 | 228.292 | 9.5533 | 292.258 | 10.2209 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.1168 | 30.2403 | 11.8281 | 13.9067 | 16.6847 | 17.5633 | 25.8037 | 6.7545 | 31.3912 | 8.1657 | 34.4852 | 17.9335 | 49.1831 | 10.8486 | 54.9572 | 26.5504 | 71.993 | 20.0042 | 107.941 | 9.8815 | 139.854 | 5.6824 | 176.375 | 9.0006 | 223.995 | 11.0553 | 286.757 | 11.6182 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.1025 | 36.8865 | 11.687 | 15.5897 | 16.5352 | 19.7671 | 25.1665 | 7.3059 | 30.7696 | 8.8148 | 34.1421 | 20.4056 | 48.2574 | 12.3563 | 54.5738 | 32.2252 | 71.3479 | 22.5815 | 105.803 | 11.4464 | 137.496 | 6.2385 | 173.922 | 10.0099 | 219.779 | 12.7934 | 281.36 | 13.4182 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.0955 | 50.0391 | 11.5939 | 17.4763 | 16.3871 | 22.2475 | 24.6929 | 7.871 | 30.1904 | 9.6967 | 33.8024 | 24.3523 | 47.3018 | 14.3274 | 54.5738 | 39.779 | 70.4263 | 26.5241 | 103.916 | 13.4315 | 135.043 | 6.9588 | 170.649 | 11.2324 | 215.427 | 15.1922 | 276.617 | 15.3439 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.0671 | 63.8269 | 11.513 | 19.7868 | 16.2565 | 25.264 | 24.2281 | 8.4378 | 29.7409 | 10.395 | 33.6001 | 28.604 | 46.5975 | 16.58 | 54.5738 | 49.0548 | 69.7953 | 30.4816 | 101.96 | 16.3024 | 132.502 | 7.7778 | 167.94 | 12.5917 | 210.739 | 18.2027 | 272.226 | 17.4243 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.0601 | 90.0953 | 11.4556 | 22.0933 | 16.1431 | 28.6325 | 23.8435 | 9.1539 | 29.2688 | 11.435 | 33.533 | 33.6984 | 45.8578 | 19.6887 | 54.5738 | 65.1077 | 69.17 | 35.3792 | 99.443 | 21.2327 | 130.529 | 8.6414 | 165.771 | 14.0316 | 206.359 | 22.8296 | 267.905 | 20.0639 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.0601 | 116.067 | 11.3756 | 25.5415 | 16.0465 | 32.0656 | 23.465 | 9.9702 | 28.9776 | 12.2951 | 33.466 | 39.2297 | 45.4469 | 23.3572 | 54.5738 | 85.4747 | 68.4817 | 43.4992 | 98.0604 | 25.5415 | 128.457 | 9.6967 | 163.466 | 15.497 | 202.678 | 28.5473 | 262.337 | 24.2316 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.053 | 163.024 | 11.3529 | 29.9414 | 15.9346 | 37.2177 | 23.0695 | 10.9243 | 28.7179 | 13.312 | 33.2991 | 47.1438 | 44.9947 | 27.4352 | 54.5738 | 123.563 | 67.8681 | 54.2856 | 96.9876 | 30.0606 | 126.544 | 10.881 | 161.355 | 17.4937 | 199.062 | 34.9253 | 258.69 | 27.7642 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.053 | 213.172 | 11.3416 | 34.5801 | 15.8868 | 42.8984 | 22.7943 | 11.8279 | 28.347 | 15.2073 | 33.1661 | 57.0499 | 44.5916 | 32.8392 | 54.5738 | 169.969 | 67.3273 | 67.7467 | 95.7349 | 36.8133 | 124.91 | 12.0892 | 159.43 | 19.7279 | 195.706 | 45.9418 | 255.093 | 32.1293 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.053 | 316.542 | 11.3416 | 40.6983 | 15.8551 | 49.3971 | 22.5224 | 12.9597 | 28.2904 | 17.4589 | 33.0668 | 69.1061 | 44.3691 | 38.9966 | 54.5738 | 227.843 | 66.8576 | 88.4108 | 94.972 | 43.0692 | 123.173 | 13.976 | 157.528 | 22.4027 | 192.6 | 59.2446 | 251.547 | 37.107 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.053 | 409.823 | 11.3416 | 49.5445 | 15.8551 | 57.5622 | 22.276 | 14.0735 | 28.2904 | 20.224 | 32.9677 | 84.6298 | 44.1478 | 49.348 | 54.5738 | 306.029 | 66.3248 | 117.226 | 93.8391 | 52.7965 | 121.339 | 16.0453 | 155.805 | 26.0023 | 189.732 | 75.644 | 248.049 | 42.8984 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.053 | 484.254 | 11.3416 | 59.836 | 15.8393 | 69.0375 | 22.1206 | 15.4509 | 28.2904 | 24.1355 | 32.9019 | 98.1303 | 44.0596 | 60.1339 | 54.5193 | 429.411 | 66.1262 | 161.252 | 92.9983 | 67.2105 | 119.892 | 18.772 | 154.1 | 29.236 | 187.282 | 94.9657 | 245.09 | 48.4735 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.053 | 543.396 | 11.3416 | 74.5993 | 15.8393 | 82.0635 | 21.9883 | 16.9969 | 28.2904 | 28.775 | 32.9019 | 119.935 | 44.0596 | 76.7033 | 54.5193 | 520.674 | 65.8622 | 210.437 | 91.9809 | 85.9003 | 118.343 | 21.9839 | 152.262 | 34.3405 | 184.678 | 124.301 | 242.167 | 56.3179 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.053 | 600.146 | 11.3416 | 93.7472 | 15.8393 | 100.398 | 21.8786 | 18.6976 | 28.2904 | 34.9947 | 32.9019 | 146.877 | 44.0156 | 103.846 | 54.5193 | 577.34 | 65.8622 | 270.563 | 91.3392 | 104.987 | 117.166 | 25.3897 | 150.446 | 40.8198 | 182.657 | 159.341 | 239.039 | 64.5282 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.053 | 600.146 | 11.3416 | 118.632 | 15.8393 | 118.044 | 21.8786 | 20.9811 | 28.2904 | 45.4426 | 32.9019 | 184.393 | 43.9716 | 130.761 | 54.5193 | 600.146 | 65.8622 | 332.66 | 90.7928 | 126.67 | 116.116 | 29.6454 | 148.502 | 53.5359 | 181.202 | 207.119 | 235.951 | 76.7033 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.053 | 600.146 | 11.3416 | 149.082 | 15.8393 | 137.967 | 21.8786 | 23.6607 | 28.2904 | 58.8925 | 32.9019 | 229.432 | 43.796 | 176.508 | 54.5193 | 600.146 | 65.8622 | 414.738 | 90.34 | 155.124 | 114.846 | 35.8747 | 147.319 | 64.1447 | 179.938 | 258.735 | 233.37 | 88.851 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.053 | 600.146 | 11.3302 | 202.24 | 15.8393 | 162.862 | 21.8786 | 38.5728 | 28.2904 | 74.6735 | 32.9019 | 271.64 | 43.7523 | 238.732 | 54.5193 | 600.146 | 65.8622 | 491.035 | 89.7995 | 201.638 | 113.93 | 42.8133 | 146.145 | 76.4751 | 178.683 | 326.117 | 230.817 | 101.602 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.053 | 600.146 | 11.3302 | 258.992 | 15.8393 | 201.838 | 21.8786 | 80.1302 | 28.2904 | 86.7578 | 32.9019 | 367.037 | 43.6649 | 305.422 | 54.5193 | 600.146 | 65.8622 | 565.983 | 89.3516 | 255.669 | 113.023 | 51.964 | 144.836 | 98.1303 | 177.436 | 415.15 | 228.063 | 122.22 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.053 | 600.146 | 11.3302 | 319.702 | 15.8393 | 248.162 | 21.8786 | 156.052 | 28.2904 | 108.163 | 32.9019 | 453.524 | 43.6212 | 375.52 | 54.5193 | 600.146 | 65.8622 | 600.146 | 88.7283 | 336.315 | 112.459 | 61.158 | 143.969 | 115.492 | 176.375 | 498.902 | 225.794 | 146.877 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.053 | 600.146 | 11.3302 | 399.771 | 15.8393 | 305.725 | 21.8786 | 346.833 | 28.2904 | 129.726 | 32.9019 | 529.541 | 43.4471 | 473.786 | 54.5193 | 600.146 | 65.8622 | 600.146 | 88.2857 | 422.22 | 111.563 | 74.9708 | 142.822 | 141.015 | 175.846 | 559.277 | 223.547 | 178.27 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.053 | 600.146 | 11.3302 | 488.602 | 15.8393 | 366.673 | 21.8786 | 600.146 | 28.2904 | 164.488 | 32.9019 | 572.77 | 43.3602 | 550.458 | 54.5193 | 600.146 | 65.8622 | 600.146 | 87.8454 | 513.993 | 111.228 | 87.1032 | 142.252 | 170.815 | 175.144 | 600.146 | 221.323 | 209.187 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.053 | 600.146 | 11.3302 | 571.066 | 15.8393 | 436.29 | 21.8786 | 600.146 | 28.2904 | 205.684 | 32.9019 | 600.146 | 43.2736 | 600.146 | 54.5193 | 600.146 | 65.8622 | 600.146 | 87.6699 | 578.488 | 110.674 | 106.035 | 141.826 | 216.372 | 175.144 | 600.146 | 219.999 | 251.638 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.053 | 600.146 | 11.3302 | 600.146 | 15.8393 | 503.882 | 21.8786 | 600.146 | 28.2904 | 248.409 | 32.9019 | 600.146 | 43.2736 | 600.146 | 54.5193 | 600.146 | 65.8622 | 600.146 | 87.4947 | 600.146 | 110.232 | 127.554 | 141.684 | 278.747 | 175.144 | 600.146 | 218.683 | 299.117 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.053 | 600.146 | 11.3302 | 600.146 | 15.8234 | 573.34 | 21.8786 | 600.146 | 28.2904 | 301.803 | 32.9019 | 600.146 | 43.2736 | 600.146 | 54.5193 | 600.146 | 65.8622 | 600.146 | 87.4947 | 600.146 | 109.902 | 173.897 | 141.26 | 359.46 | 175.144 | 600.146 | 217.592 | 361.968 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.053 | 600.146 | 11.3302 | 600.146 | 15.8234 | 600.146 | 21.8786 | 600.146 | 28.2904 | 377.765 | 32.9019 | 600.146 | 43.2736 | 600.146 | 54.5193 | 600.146 | 65.8622 | 600.146 | 87.4947 | 600.146 | 109.572 | 223.583 | 141.26 | 461.247 | 175.144 | 600.146 | 216.29 | 446.816 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.053 | 600.146 | 11.3302 | 600.146 | 15.8234 | 600.146 | 21.8786 | 600.146 | 28.2904 | 467.242 | 32.9019 | 600.146 | 43.2736 | 600.146 | 54.5193 | 600.146 | 65.8622 | 600.146 | 87.4947 | 600.146 | 109.353 | 282.651 | 141.26 | 569.367 | 175.144 | 600.146 | 215.427 | 553.749 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.053 | 600.146 | 11.3302 | 600.146 | 15.8234 | 600.146 | 21.8786 | 600.146 | 28.2904 | 552.65 | 32.9019 | 600.146 | 43.2736 | 600.146 | 54.5193 | 600.146 | 65.8622 | 600.146 | 87.4947 | 600.146 | 108.917 | 347.868 | 141.118 | 600.146 | 175.144 | 600.146 | 214.567 | 600.146 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.053 | 600.146 | 11.3302 | 600.146 | 15.8234 | 600.146 | 21.8786 | 600.146 | 28.2904 | 600.146 | 32.9019 | 600.146 | 43.2736 | 600.146 | 54.5193 | 600.146 | 65.8622 | 600.146 | 87.4947 | 600.146 | 108.482 | 424.744 | 141.118 | 600.146 | 175.144 | 600.146 | 214.567 | 600.146 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.053 | 600.146 | 11.3302 | 600.146 | 15.8234 | 600.146 | 21.8786 | 600.146 | 28.2904 | 600.146 | 32.9019 | 600.146 | 43.2736 | 600.146 | 54.5193 | 600.146 | 65.8622 | 600.146 | 87.4947 | 600.146 | 108.157 | 488.117 | 141.118 | 600.146 | 175.144 | 600.146 | 214.567 | 600.146 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.053 | 600.146 | 11.3302 | 600.146 | 15.8234 | 600.146 | 21.8786 | 600.146 | 28.2904 | 600.146 | 32.9019 | 600.146 | 43.2736 | 600.146 | 54.5193 | 600.146 | 65.8622 | 600.146 | 87.4947 | 600.146 | 107.833 | 568.802 | 141.118 | 600.146 | 175.144 | 600.146 | 214.567 | 600.146 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969
7.053 | 600.146 | 11.3302 | 600.146 | 15.8234 | 600.146 | 21.8786 | 600.146 | 28.2904 | 600.146 | 32.9019 | 600.146 | 43.2736 | 600.146 | 54.5193 | 600.146 | 65.8622 | 600.146 | 87.4947 | 600.146 | 107.725 | 600.146 | 141.118 | 600.146 | 175.144 | 600.146 | 214.567 | 600.146 | 294.89 | 590.26 | 361.219 | 592.969 | 424.582 | 593.309 | 480.534 | 592.969