## 153_4
S&C Power Fuses - Types SM-4 and SM-5 | [9 empty] | S&C Power Fuses - Types SM-4 and SM-5 | [9 empty] | S&C Power Fuses - Types SM-4 and SM-5 | [9 empty] | S&C Power Fuses - Types SM-4 and SM-5 | [9 empty] | S&C Power Fuses - Types SM-4 and SM-5
Standard Speed (TCC 153-4) | [9 empty] | Standard Speed (TCC 153-4) | [9 empty] | Standard Speed (TCC 153-4) | [9 empty] | Standard Speed (TCC 153-4) | [9 empty] | Standard Speed (TCC 153-4)
Minimum Melting Time-Current Characteristic Curves Dated June 17, 1991 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated June 17, 1991 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated June 17, 1991 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated June 17, 1991 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated June 17, 1991
Tolerance in Terms of Current: |  |  | Plus 10% for fuse units rated 10E thru 400E | [6 empty] | Tolerance in Terms of Current: |  |  | Plus 10% for fuse units rated 10E thru 400E | [6 empty] | Tolerance in Terms of Current: |  |  | Plus 10% for fuse units rated 10E thru 400E | [6 empty] | Tolerance in Terms of Current: |  |  | Plus 10% for fuse units rated 10E thru 400E | [6 empty] | Tolerance in Terms of Current: |  |  | Plus 10% for fuse units rated 10E thru 400E
|  |  | Plus 15% for fuse units rated 5E thru 7E | [9 empty] | Plus 15% for fuse units rated 5E thru 7E | [9 empty] | Plus 15% for fuse units rated 5E thru 7E | [9 empty] | Plus 15% for fuse units rated 5E thru 7E | [9 empty] | Plus 15% for fuse units rated 5E thru 7E
|  |  | Plus 20% for fuse units rated 3E | [9 empty] | Plus 20% for fuse units rated 3E | [9 empty] | Plus 20% for fuse units rated 3E | [9 empty] | Plus 20% for fuse units rated 3E | [9 empty] | Plus 20% for fuse units rated 3E
3E |  | 5E |  | 7E |  | 10E |  | 13E |  | 15E |  | 20E |  | 25E |  | 30E |  | 40E |  | 50E |  | 65E |  | 80E |  | 100E |  | 125E |  | 150E |  | 175E |  | 200E |  | 250E |  | 300E |  | 400E |  | 2-250E |  | 2-300E |  | 2-400E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
79.9926 | 0.01 | 246.64 | 0.01 | 359.219 | 0.01 | 490.748 | 0.01 | 630.764 | 0.01 | 744.662 | 0.01 | 966.741 | 0.01 | 1255.05 | 0.01 | 1498.06 | 0.01 | 1844.43 | 0.01 | 2225.93 | 0.01 | 3074.59 | 0.01 | 3710.52 | 0.01 | 4717 | 0.01 | 6247.45 | 0.01 | 7615.4 | 0.01 | 8274.45 | 0.01 | 9089.98 | 0.01 | 11315.4 | 0.01 | 14529.3 | 0.01 | 17710.7 | 0.01 | 20494.8 | 0.01 | 25794.7 | 0.01 | 32110.1 | 0.01
73.6213 | 0.011818 | 222.278 | 0.012423 | 291.468 | 0.015159 | 428.775 | 0.013378 | 517.459 | 0.015357 | 637.103 | 0.013882 | 776.604 | 0.015715 | 1018.34 | 0.015296 | 1203.42 | 0.015605 | 1498.06 | 0.015512 | 1806.1 | 0.015388 | 2469.89 | 0.015543 | 3010.7 | 0.015434 | 3747.81 | 0.01573 | 5018.71 | 0.015667 | 6056.75 | 0.015872 | 6653.7 | 0.015434 | 7229.52 | 0.015667 | 9089.98 | 0.015683 | 11683.4 | 0.015543 | 14384.8 | 0.015605 | 16480.4 | 0.015952 | 20929.7 | 0.015512 | 25512.5 | 0.015952
64.9705 | 0.015189 | 198.131 | 0.01573 | 234.143 | 0.023989 | 351.754 | 0.020117 | 428.775 | 0.022569 | 517.459 | 0.02117 | 623.863 | 0.024498 | 835.417 | 0.022933 | 997.179 | 0.023094 | 1228.96 | 0.023373 | 1466.93 | 0.023397 | 2113.14 | 0.021426 | 2445.31 | 0.023821 | 3074.59 | 0.023443 | 4076.23 | 0.023941 | 4865.52 | 0.024843 | 5398.78 | 0.023917 | 5749.85 | 0.025168 | 7457.15 | 0.023608 | 9575.16 | 0.023257 | 11683.4 | 0.023774 | 13372.1 | 0.024254 | 16999.3 | 0.02349 | 20494.8 | 0.024596
57.3363 | 0.019917 | 167.826 | 0.021706 | 169.513 | 0.046599 | 259.805 | 0.036583 | 330.277 | 0.038497 | 428.775 | 0.030957 | 485.865 | 0.040837 | 685.351 | 0.033906 | 809.916 | 0.03529 | 966.741 | 0.037886 | 1203.42 | 0.035184 | 1733.55 | 0.032091 | 1964.37 | 0.037099 | 2445.31 | 0.038 | 3238.7 | 0.037397 | 3947.86 | 0.038152 | 4246.83 | 0.038267 | 4618.98 | 0.03904 | 5990.49 | 0.03662 | 7699.63 | 0.036547 | 9479.89 | 0.035966 | 10414.2 | 0.03967 | 13793.1 | 0.036474 | 16480.4 | 0.038652
50.5991 | 0.02532 | 142.015 | 0.030895 | 118.977 | 0.093185 | 208.916 | 0.057719 | 231.813 | 0.07637 | 351.754 | 0.046646 | 394.229 | 0.061657 | 550.557 | 0.053016 | 657.162 | 0.052804 | 793.085 | 0.056407 | 966.741 | 0.055345 | 1436.45 | 0.047731 | 1562.32 | 0.057893 | 1964.37 | 0.05865 | 2547.65 | 0.060739 | 3171.4 | 0.058358 | 3483.97 | 0.057777 | 3789.27 | 0.059003 | 4764.41 | 0.058826 | 6056.75 | 0.058885 | 7777.02 | 0.054033 | 8274.45 | 0.063535 | 10635.2 | 0.061472 | 13239 | 0.059955
45.1023 | 0.032349 | 116.504 | 0.045087 | 90.7341 | 0.16461 | 180.536 | 0.075989 | 178.561 | 0.13131 | 291.468 | 0.068552 | 320.195 | 0.094405 | 451.661 | 0.078382 | 550.557 | 0.076141 | 637.103 | 0.088641 | 776.604 | 0.085763 | 1153.93 | 0.073229 | 1307.57 | 0.083897 | 1562.32 | 0.092721 | 2048.63 | 0.095163 | 2575.83 | 0.089442 | 2770.9 | 0.091523 | 3010.7 | 0.093092 | 3827.35 | 0.092258 | 4764.41 | 0.095736 | 6185.28 | 0.086193 | 6515.43 | 0.10227 | 8274.45 | 0.10135 | 10518.8 | 0.09431
39.8027 | 0.041124 | 94.5316 | 0.070358 | 67.0162 | 0.30024 | 156.012 | 0.10371 | 148.106 | 0.19068 | 241.756 | 0.099942 | 259.805 | 0.14527 | 370.529 | 0.1174 | 456.2 | 0.11123 | 506.706 | 0.13763 | 610.899 | 0.1375 | 946.651 | 0.11001 | 1039.95 | 0.13197 | 1267.66 | 0.14253 | 1645.71 | 0.14776 | 2090.02 | 0.13545 | 2225.93 | 0.14197 | 2445.31 | 0.13985 | 3044 | 0.14527 | 3789.27 | 0.15029 | 5018.71 | 0.12923 | 5074.22 | 0.16929 | 6788.11 | 0.1518 | 8365.97 | 0.1485
35.4788 | 0.052488 | 79.1966 | 0.099344 | 41.51 | 0.78808 | 126.587 | 0.15518 | 121.38 | 0.28646 | 196.16 | 0.15044 | 211.015 | 0.21955 | 297.654 | 0.18066 | 366.475 | 0.17462 | 415.686 | 0.20843 | 490.748 | 0.2137 | 793.085 | 0.15721 | 853.146 | 0.19806 | 1018.34 | 0.21585 | 1335.32 | 0.22737 | 1697.53 | 0.20864 | 1750.97 | 0.23104 | 2006.06 | 0.20801 | 2445.31 | 0.22176 | 2918.8 | 0.25585 | 4117.2 | 0.19259 | 4031.64 | 0.26736 | 5398.78 | 0.23903 | 6720.57 | 0.23058
30.3542 | 0.071994 | 65.6235 | 0.14556 | 32.9811 | 1.2434 | 104.997 | 0.22692 | 99.5772 | 0.4168 | 162.541 | 0.21977 | 173.111 | 0.32623 | 239.112 | 0.27883 | 300.645 | 0.25636 | 337.286 | 0.31406 | 386.422 | 0.34988 | 650.623 | 0.2315 | 685.351 | 0.30692 | 818.056 | 0.33819 | 1072.69 | 0.34918 | 1392.6 | 0.31125 | 1436.45 | 0.34467 | 1627.71 | 0.31469 | 2026.22 | 0.32819 | 2445.31 | 0.36856 | 3377.63 | 0.28446 | 3274.53 | 0.41389 | 4117.2 | 0.40895 | 5398.78 | 0.35802
26.2308 | 0.095353 | 52.1922 | 0.23313 | 29.7234 | 1.5696 | 87.8766 | 0.32721 | 74.4356 | 0.75793 | 134.819 | 0.32298 | 142.015 | 0.48716 | 186.22 | 0.45605 | 251.875 | 0.36856 | 270.949 | 0.4857 | 317.009 | 0.52615 | 562.241 | 0.3125 | 562.241 | 0.46526 | 650.623 | 0.53571 | 880.008 | 0.51522 | 1129.95 | 0.46759 | 1178.42 | 0.51163 | 1335.32 | 0.47041 | 1788.13 | 0.4168 | 2026.22 | 0.54326 | 2798.75 | 0.41596 | 2656.93 | 0.62615 | 3307.43 | 0.63435 | 4384.93 | 0.55037
23.8774 | 0.11752 | 39.8027 | 0.39607 | 25.9698 | 2.0562 | 69.8908 | 0.52353 | 57.3363 | 1.2902 | 104.997 | 0.53304 | 115.23 | 0.74144 | 174.85 | 0.5204 | 202.336 | 0.57169 | 220.067 | 0.75039 | 265.319 | 0.76097 | 465.881 | 0.45287 | 451.661 | 0.72169 | 527.913 | 0.83597 | 721.932 | 0.76862 | 966.741 | 0.63753 | 987.257 | 0.72531 | 1129.95 | 0.66687 | 1513.12 | 0.6016 | 1864.83 | 0.64008 | 2344.74 | 0.5986 | 2225.93 | 0.93785 | 2798.75 | 0.91653 | 3908.58 | 0.71166
19.805 | 0.16997 | 31.6562 | 0.63625 | 23.8774 | 2.5039 | 56.7091 | 0.79839 | 48.0352 | 1.9133 | 85.1942 | 0.80239 | 95.5771 | 1.0885 | 159.322 | 0.6388 | 164.339 | 0.87096 | 180.536 | 1.1217 | 246.64 | 0.90289 | 390.306 | 0.65301 | 398.589 | 0.95393 | 465.881 | 1.0875 | 604.82 | 1.1535 | 793.085 | 0.95298 | 907.715 | 0.86748 | 1018.34 | 0.83681 | 1350.09 | 0.77247 | 1645.71 | 0.85116 | 2069.22 | 0.79999 | 1984.11 | 1.231 | 2497.21 | 1.1958 | 3411.57 | 0.95298
17.1146 | 0.23104 | 25.1519 | 0.99984 | 21.9756 | 3.0674 | 49.5476 | 1.0521 | 43.2473 | 2.4347 | 68.4384 | 1.2672 | 79.9926 | 1.5602 | 145.028 | 0.77016 | 137.68 | 1.2596 | 157.58 | 1.4708 | 234.143 | 1.0324 | 317.009 | 1.0221 | 362.829 | 1.1851 | 411.139 | 1.436 | 517.459 | 1.6013 | 657.162 | 1.426 | 835.417 | 1.0521 | 937.232 | 1.0262 | 1215.52 | 0.97223 | 1452.33 | 1.0951 | 1864.83 | 0.99386 | 1844.43 | 1.5051 | 2296.01 | 1.4723 | 2918.8 | 1.3824
15.2554 | 0.29726 | 20.6339 | 1.5248 | 20.8621 | 3.5567 | 41.9272 | 1.5248 | 40.2027 | 2.9091 | 62.9874 | 1.537 | 67.0162 | 2.3346 | 136.174 | 0.89122 | 123.956 | 1.5838 | 146.486 | 1.7786 | 213.136 | 1.2698 | 294.692 | 1.2103 | 333.93 | 1.4475 | 366.475 | 1.9057 | 471.034 | 2.0255 | 586.358 | 1.8661 | 776.604 | 1.2546 | 853.146 | 1.266 | 1062.02 | 1.3335 | 1335.32 | 1.3755 | 1714.59 | 1.231 | 1680.64 | 1.9384 | 2069.22 | 1.9736 | 2630.5 | 1.7911
13.8867 | 0.37375 | 17.8309 | 2.0872 | 19.1813 | 4.3922 | 36.2317 | 2.1315 | 37.7858 | 3.4344 | 58.5531 | 1.8328 | 62.9874 | 2.7839 | 125.327 | 1.0543 | 111.713 | 2.0235 | 136.174 | 2.1465 | 198.131 | 1.5309 | 270.949 | 1.4738 | 310.422 | 1.7451 | 320.195 | 2.7016 | 437.874 | 2.4445 | 545.079 | 2.2633 | 714.749 | 1.5187 | 793.085 | 1.5309 | 957.122 | 1.7451 | 1215.52 | 1.7226 | 1593.88 | 1.4827 | 1529.85 | 2.4889 | 1904.41 | 2.4274 | 2418.56 | 2.3068
12.133 | 0.51009 | 15.2554 | 3.1076 | 18.4107 | 4.9721 | 32.6529 | 2.7617 | 35.1257 | 4.199 | 54.978 | 2.1103 | 59.1416 | 3.363 | 115.23 | 1.2787 | 100.678 | 2.6534 | 126.587 | 2.6113 | 184.183 | 1.8792 | 254.66 | 1.7486 | 288.568 | 2.081 | 300.645 | 3.2833 | 407.048 | 3.0369 | 511.799 | 2.6774 | 671.109 | 1.7965 | 721.932 | 1.9461 | 907.715 | 2.0623 | 1118.7 | 2.1573 | 1466.93 | 1.8109 | 1452.33 | 2.9977 | 1788.13 | 2.9442 | 2248.3 | 2.8486
11.0445 | 0.65236 | 13.8867 | 4.0222 | 17.4604 | 5.9408 | 31.3099 | 3.1767 | 33.3459 | 4.9771 | 51.6729 | 2.4666 | 54.978 | 4.1864 | 107.118 | 1.5006 | 94.5316 | 3.1831 | 117.675 | 3.1608 | 171.217 | 2.3068 | 239.112 | 2.0541 | 270.949 | 2.5039 | 288.568 | 3.8108 | 390.306 | 3.5143 | 485.865 | 3.2441 | 623.863 | 2.1811 | 671.109 | 2.4691 | 827.104 | 2.6534 | 1029.6 | 2.6747 | 1350.09 | 2.2747 | 1392.6 | 3.431 | 1680.64 | 3.7391 | 2113.14 | 3.5038
10.0536 | 0.841 | 12.9091 | 4.903 | 16.9274 | 6.8267 | 28.8161 | 4.0182 | 32.328 | 5.8994 | 49.0546 | 2.7811 | 51.6729 | 5.0573 | 97.6055 | 1.8073 | 87.8766 | 3.8878 | 112.948 | 3.7503 | 160.924 | 2.8203 | 224.737 | 2.4299 | 254.66 | 3.0613 | 270.949 | 4.7296 | 374.253 | 4.2116 | 465.881 | 3.7654 | 592.251 | 2.5189 | 623.863 | 3.0766 | 785.194 | 3.1545 | 966.741 | 3.2898 | 1267.66 | 2.7507 | 1350.09 | 3.9112 | 1593.88 | 4.4364 | 2048.63 | 4.1406
9.3459 | 1.0521 | 12.255 | 6.1709 | 16.2474 | 8.2552 | 27.0567 | 4.8932 | 31.3099 | 7.0487 | 47.037 | 3.1958 | 50.0456 | 5.9825 | 91.646 | 2.1401 | 83.4238 | 4.6779 | 107.118 | 4.4765 | 151.098 | 3.4139 | 213.136 | 2.8744 | 241.756 | 3.5781 | 262.679 | 5.6964 | 359.219 | 5.0827 | 447.167 | 4.3529 | 567.892 | 2.9442 | 586.358 | 3.9269 | 744.662 | 3.8261 | 917.755 | 3.9269 | 1203.42 | 3.2474 | 1294.56 | 4.5125 | 1529.85 | 5.3433 | 1964.37 | 4.9771
8.5074 | 1.4217 | 11.8809 | 7.2199 | 15.7357 | 9.7947 | 26.2308 | 5.6908 | 30.0521 | 8.5921 | 44.1651 | 3.8491 | 48.518 | 6.9855 | 86.0505 | 2.4989 | 81.6902 | 5.0624 | 102.815 | 5.2954 | 143.442 | 4.1076 | 202.336 | 3.3429 | 231.813 | 4.22 | 254.66 | 7.2779 | 347.906 | 5.9885 | 428.775 | 5.3647 | 550.557 | 3.2964 | 562.241 | 4.7533 | 721.932 | 4.4676 | 871.252 | 4.7867 | 1153.93 | 3.853 | 1241.32 | 5.3007 | 1452.33 | 6.7927 | 1904.41 | 5.9467
8.0763 | 1.7174 | 11.5067 | 8.7307 | 15.2554 | 11.5981 | 25.1519 | 6.8063 | 29.1057 | 10.8248 | 41.9272 | 4.4989 | 47.037 | 8.247 | 79.9926 | 2.9977 | 78.4086 | 6.0608 | 99.5772 | 6.0427 | 139.063 | 4.7867 | 192.084 | 3.8684 | 222.278 | 4.9721 | 246.64 | 8.7832 | 337.286 | 7.0699 | 415.686 | 6.2579 | 527.913 | 3.8108 | 539.116 | 5.8407 | 692.239 | 5.3167 | 835.417 | 5.5614 | 1107.57 | 4.5578 | 1215.52 | 6.0851 | 1392.6 | 8.3884 | 1844.43 | 7.2127
7.6671 | 2.1942 | 11.2789 | 10.1436 | 14.9384 | 14.5828 | 24.3842 | 8.2305 | 28.2173 | 13.3811 | 40.2027 | 5.201 | 45.6012 | 9.8438 | 75.1837 | 3.6431 | 74.4356 | 7.6358 | 96.5377 | 7.4547 | 133.344 | 5.725 | 186.22 | 4.4099 | 215.494 | 5.9646 | 239.112 | 10.7064 | 330.277 | 8.3716 | 407.048 | 7.4398 | 511.799 | 4.4497 | 527.913 | 7.1481 | 671.109 | 6.2893 | 801.056 | 6.7251 | 1072.69 | 5.322 | 1190.26 | 7.1911 | 1350.09 | 10.1842 | 1788.13 | 8.9338
7.6671 | 2.2498 | 10.9237 | 12.5264 | 14.6279 | 17.0618 | 23.6399 | 9.8537 | 27.9365 | 16.0201 | 38.5877 | 6.2267 | 44.6536 | 11.7499 | 70.5932 | 4.3053 | 72.0913 | 9.4201 | 94.5316 | 8.8626 | 129.273 | 6.6449 | 178.561 | 5.2375 | 208.916 | 6.9646 | 234.143 | 13.1819 | 320.195 | 10.5259 | 394.229 | 8.9338 | 490.748 | 5.4349 | 506.706 | 9.2336 | 650.623 | 7.6129 | 768.877 | 8.1567 | 1039.95 | 6.5853 | 1153.93 | 8.7045 | 1322.03 | 12.3153 | 1750.97 | 10.9994
7.3517 | 2.7507 | 10.5902 | 16.5907 | 14.4824 | 20.4676 | 22.9183 | 12.0353 | 27.3559 | 20.6733 | 37.3725 | 7.4622 | 43.7256 | 14.612 | 67.0162 | 5.3326 | 69.8908 | 11.5287 | 91.646 | 11.0435 | 125.327 | 7.79 | 171.217 | 6.1401 | 202.336 | 8.4473 | 229.277 | 17.4413 | 313.541 | 13.0507 | 386.422 | 10.9774 | 475.768 | 6.2267 | 490.748 | 12.0835 | 630.764 | 9.62 | 744.662 | 10.225 | 1008.2 | 8.1079 | 1129.95 | 10.4734 | 1280.4 | 15.6402 | 1714.59 | 13.8855
7.0564 | 3.5003 | 10.4849 | 20.777 | 14.324 | 24.2119 | 22.442 | 14.7588 | 27.0567 | 25.6577 | 35.8712 | 9.4768 | 42.817 | 18.8562 | 63.6204 | 6.4163 | 67.7574 | 14.4233 | 89.7415 | 13.341 | 121.38 | 9.5625 | 165.99 | 7.2779 | 196.16 | 10.5364 | 224.737 | 21.7116 | 307.026 | 16.724 | 378.392 | 13.8855 | 465.881 | 7.4101 | 481.031 | 15.2998 | 617.656 | 12.2784 | 721.932 | 13.2083 | 976.457 | 10.5681 | 1095.46 | 12.9597 | 1255.05 | 20.8811 | 1680.64 | 17.3717
6.8342 | 4.2454 | 10.3702 | 25.0743 | 14.1814 | 30.3819 | 21.9756 | 18.2624 | 26.7875 | 31.9715 | 34.3958 | 12.0353 | 41.9272 | 24.5287 | 61.6784 | 7.5674 | 65.6235 | 19.1412 | 88.8486 | 15.6558 | 117.675 | 12.0353 | 162.541 | 8.2883 | 190.172 | 13.2083 | 222.278 | 27.5732 | 300.645 | 21.6249 | 370.529 | 17.6872 | 451.661 | 9.2706 | 475.768 | 18.7247 | 598.204 | 18.2077 | 699.895 | 17.8471 | 946.651 | 14.7294 | 1062.02 | 17.5639 | 1215.52 | 30.2303 | 1662.25 | 21.4311
6.6256 | 5.322 | 10.267 | 31.4955 | 14.1814 | 33.6781 | 21.5189 | 23.1929 | 26.4944 | 40.1189 | 33.681 | 14.8774 | 41.51 | 32.3899 | 60.3967 | 9.0326 | 64.3241 | 25.1748 | 86.0505 | 20.6527 | 114.083 | 15.3305 | 157.58 | 9.8143 | 186.22 | 15.5311 | 217.659 | 35.9039 | 294.692 | 27.9061 | 362.829 | 23.4963 | 437.874 | 11.7852 | 465.881 | 23.3091 | 579.944 | 25.6065 | 685.351 | 25.1748 | 926.979 | 19.4499 | 1039.95 | 23.6614 | 1203.42 | 39.5611 | 1645.71 | 28.046
6.4879 | 6.5985 | 10.1547 | 42.0075 | 14.1814 | 46.2864 | 21.3048 | 30.2001 | 26.2308 | 50.7975 | 32.328 | 21.0278 | 41.0559 | 41.5064 | 57.9125 | 11.3231 | 63.6204 | 31.9715 | 84.3465 | 25.301 | 110.601 | 20.0223 | 152.77 | 11.9513 | 182.35 | 18.3723 | 213.136 | 48.2236 | 291.468 | 36.2285 | 355.289 | 31.5586 | 428.775 | 14.3801 | 461.246 | 30.0195 | 574.173 | 31.5271 | 664.431 | 37.1085 | 907.715 | 26.0195 | 1029.6 | 30.0195 | 1190.26 | 53.9387 | 1611.51 | 36.9234
6.4233 | 8.0433 | 10.1547 | 62.4177 | 14.1814 | 68.8444 | 20.8621 | 41.0113 | 26.2308 | 73.615 | 31.9744 | 27.2443 | 40.6474 | 53.242 | 56.7091 | 13.9133 | 62.2983 | 42.218 | 83.4238 | 31.4955 | 107.118 | 28.987 | 148.106 | 14.6412 | 180.536 | 21.517 | 208.916 | 63.1081 | 285.411 | 48.4168 | 351.754 | 41.2581 | 419.864 | 18.3356 | 456.2 | 40.2797 | 567.892 | 44.2496 | 664.431 | 47.8872 | 898.683 | 34.2897 | 1018.34 | 41.2168 | 1178.42 | 87.606 | 1611.51 | 47.2214
6.2899 | 10.7171 | 10.1547 | 83.5838 | 14.1814 | 95.5691 | 20.6339 | 55.1937 | 26.2308 | 96.6262 | 31.3099 | 36.2648 | 40.6474 | 67.4137 | 55.5861 | 17.3197 | 61.6784 | 52.5543 | 82.5937 | 39.6403 | 104.997 | 38.2004 | 145.028 | 18.2441 | 176.784 | 27.3809 | 206.63 | 80.9514 | 282.571 | 69.4668 | 347.906 | 53.3486 | 411.139 | 23.9231 | 451.661 | 51.4622 | 556.091 | 65.03 | 657.162 | 92.4668 | 889.741 | 52.3969 | 997.179 | 60.6942 | 1178.42 | 151.388 | 1593.88 | 62.4177
6.221 | 13.8716 | 10.1547 | 115.567 | 14.1814 | 136.982 | 20.4286 | 76.3134 | 26.2308 | 132.27 | 30.9984 | 44.6051 | 40.6474 | 90.7265 | 54.431 | 21.2604 | 61.0037 | 71.3679 | 81.6902 | 53.616 | 102.815 | 52.6596 | 142.015 | 22.6655 | 173.111 | 36.0118 | 204.574 | 108.51 | 279.48 | 94.9025 | 341.017 | 74.1321 | 402.595 | 32.7154 | 447.167 | 67.5487 | 550.557 | 118.611 | 657.162 | 134.269 | 880.008 | 70.7285 | 997.179 | 84.3394 | 1178.42 | 211.632 | 1562.32 | 115.914
6.1591 | 18.0626 | 10.1547 | 164.654 | 14.1814 | 183.8 | 20.2051 | 105.725 | 26.2308 | 183.433 | 30.6592 | 56.7042 | 40.6474 | 122.223 | 53.2999 | 26.6249 | 60.3967 | 95.1876 | 80.8773 | 72.6642 | 101.69 | 67.7516 | 139.063 | 28.1021 | 171.217 | 45.5061 | 202.336 | 147.946 | 276.699 | 131.874 | 337.286 | 105.514 | 398.589 | 43.2868 | 442.275 | 106.043 | 550.557 | 185.276 | 657.162 | 186.578 | 880.008 | 99.6685 | 997.179 | 136.571 | 1178.42 | 326.964 | 1562.32 | 169.33
6.0979 | 23.2626 | 10.1547 | 234.358 | 14.1814 | 247.857 | 20.2051 | 145.307 | 26.2308 | 256.685 | 30.3542 | 65.815 | 40.6474 | 172.751 | 52.1922 | 35.7606 | 60.3967 | 110.592 | 80.8773 | 85.187 | 100.678 | 84.6774 | 136.174 | 35.9039 | 169.513 | 58.0235 | 202.336 | 158.356 | 276.699 | 189.398 | 333.93 | 142.572 | 394.229 | 61.3042 | 442.275 | 148.391 | 550.557 | 295.554 | 657.162 | 289.991 | 880.008 | 140.449 | 987.257 | 218.733 | 1178.42 | 478.116 | 1562.32 | 240.531
6.0979 | 31.5586 | 10.1547 | 331.906 | 14.1814 | 336.922 | 20.2051 | 208.273 | 26.2308 | 348.226 | 30.3542 | 87.0819 | 40.6474 | 244.655 | 51.6729 | 47.4581 | 60.3967 | 116.146 | 80.8773 | 112.488 | 100.678 | 94.9025 | 134.819 | 43.5038 | 167.826 | 75.7054 | 202.336 | 211.844 | 276.699 | 210.156 | 333.93 | 211.209 | 390.306 | 94.9025 | 437.874 | 252.358 | 545.079 | 435.22 | 657.162 | 429.599 | 880.008 | 200.106 | 987.257 | 360.99 | 1178.42 | 571.265 | 1562.32 | 333.236
6.0979 | 46.9389 | 10.1547 | 471.469 | 14.1814 | 430.029 | 20.2051 | 271.741 | 26.2308 | 464.449 | 30.3542 | 112.939 | 40.6474 | 319.53 | 51.1076 | 61.7348 | 60.3967 | 157.724 | 80.8773 | 149.732 | 100.678 | 117.666 | 133.344 | 53.7234 | 165.99 | 104.36 | 202.336 | 273.103 | 276.699 | 293.199 | 333.93 | 280.297 | 386.422 | 144.438 | 437.874 | 407.423 | 545.079 | 633.876 | 657.162 | 536.385 | 871.252 | 281.984 | 976.457 | 469.587 | 1178.42 | 571.265 | 1562.32 | 419.411
6.0979 | 67.279 | 10.1547 | 632.61 | 14.1814 | 522.619 | 20.2051 | 374.972 | 26.2308 | 635.781 | 30.3542 | 158.356 | 40.6474 | 423.203 | 50.5991 | 75.2525 | 60.3967 | 212.268 | 80.8773 | 189.398 | 100.678 | 146.181 | 130.573 | 70.0247 | 164.339 | 144.727 | 202.336 | 369.759 | 276.699 | 382.165 | 333.93 | 391.056 | 386.422 | 214.401 | 437.874 | 634.51 | 545.079 | 633.876 | 657.162 | 631.346 | 871.252 | 393.017 | 976.457 | 571.837 | 1178.42 | 571.265 | 1562.32 | 572.981
6.0979 | 102.191 | 10.1547 | 632.61 | 14.1814 | 637.691 | 20.2051 | 492.184 | 26.2308 | 635.781 | 30.3542 | 222.038 | 40.6474 | 532.111 | 50.5991 | 102.396 | 60.3967 | 289.123 | 80.8773 | 241.495 | 100.678 | 191.684 | 130.573 | 85.443 | 162.541 | 211.632 | 202.336 | 469.587 | 276.699 | 506.666 | 333.93 | 496.137 | 386.422 | 311.329 | 437.874 | 634.51 | 545.079 | 633.876 | 657.162 | 631.346 | 871.252 | 510.226 | 976.457 | 571.837 | 1178.42 | 571.265 | 1562.32 | 572.981
6.0979 | 150.784 | 10.1547 | 632.61 | 14.1814 | 637.691 | 20.2051 | 635.145 | 26.2308 | 635.781 | 30.3542 | 298.823 | 40.6474 | 638.329 | 50.5991 | 152.757 | 60.3967 | 387.94 | 80.8773 | 308.849 | 100.678 | 249.099 | 130.573 | 106.575 | 162.541 | 286.532 | 202.336 | 570.694 | 276.699 | 634.51 | 333.93 | 634.51 | 382.195 | 444.457 | 437.874 | 634.51 | 545.079 | 633.876 | 657.162 | 631.346 | 880.008 | 635.145 | 976.457 | 571.837 | 1178.42 | 571.265 | 1562.32 | 572.981
6.0979 | 210.998 | 10.1547 | 632.61 | 14.1814 | 637.691 | 20.2051 | 635.145 | 26.2308 | 635.781 | 30.3542 | 392.624 | 40.6474 | 638.329 | 50.5991 | 207.857 | 60.3967 | 438.716 | 80.8773 | 388.329 | 100.678 | 313.516 | 130.573 | 142.287 | 162.541 | 373.849 | 202.336 | 636.417 | 276.699 | 634.51 | 333.93 | 634.51 | 382.195 | 634.51 | 437.874 | 634.51 | 545.079 | 633.876 | 657.162 | 631.346 | 880.008 | 635.145 | 976.457 | 571.837 | 1178.42 | 571.265 | 1562.32 | 572.981
6.0979 | 304.25 | 10.1547 | 632.61 | 14.1814 | 637.691 | 20.2051 | 635.145 | 26.2308 | 635.781 | 30.3542 | 498.624 | 40.6474 | 638.329 | 50.5991 | 256.685 | 60.3967 | 532.111 | 80.8773 | 500.122 | 100.678 | 433.917 | 130.573 | 187.889 | 162.541 | 506.666 | 202.336 | 636.417 | 276.699 | 634.51 | 333.93 | 634.51 | 382.195 | 634.51 | 437.874 | 634.51 | 545.079 | 633.876 | 657.162 | 631.346 | 880.008 | 635.145 | 976.457 | 571.837 | 1178.42 | 571.265 | 1562.32 | 572.981
6.0979 | 407.423 | 10.1547 | 632.61 | 14.1814 | 637.691 | 20.2051 | 635.145 | 26.2308 | 635.781 | 30.3542 | 635.781 | 40.6474 | 638.329 | 50.5991 | 342.014 | 60.3967 | 635.781 | 80.8773 | 636.417 | 100.678 | 545.582 | 130.573 | 260.304 | 162.541 | 636.417 | 202.336 | 636.417 | 276.699 | 634.51 | 333.93 | 634.51 | 382.195 | 634.51 | 437.874 | 634.51 | 545.079 | 633.876 | 657.162 | 631.346 | 880.008 | 635.145 | 976.457 | 571.837 | 1178.42 | 571.265 | 1562.32 | 572.981
6.0979 | 530.517 | 10.1547 | 632.61 | 14.1814 | 637.691 | 20.2051 | 635.145 | 26.2308 | 635.781 | 30.3542 | 635.781 | 40.6474 | 638.329 | 50.5991 | 438.716 | 60.3967 | 635.781 | 80.8773 | 636.417 | 100.678 | 637.691 | 130.573 | 367.547 | 162.541 | 636.417 | 202.336 | 636.417 | 276.699 | 634.51 | 333.93 | 634.51 | 382.195 | 634.51 | 437.874 | 634.51 | 545.079 | 633.876 | 657.162 | 631.346 | 880.008 | 635.145 | 976.457 | 571.837 | 1178.42 | 571.265 | 1562.32 | 572.981
6.0979 | 636.417 | 10.1547 | 632.61 | 14.1814 | 637.691 | 20.2051 | 635.145 | 26.2308 | 635.781 | 30.3542 | 635.781 | 40.6474 | 638.329 | 50.5991 | 532.111 | 60.3967 | 635.781 | 80.8773 | 636.417 | 100.678 | 637.691 | 130.573 | 474.78 | 162.541 | 636.417 | 202.336 | 636.417 | 276.699 | 634.51 | 333.93 | 634.51 | 382.195 | 634.51 | 437.874 | 634.51 | 545.079 | 633.876 | 657.162 | 631.346 | 880.008 | 635.145 | 976.457 | 571.837 | 1178.42 | 571.265 | 1562.32 | 572.981
6.0979 | 636.417 | 10.1547 | 632.61 | 14.1814 | 637.691 | 20.2051 | 635.145 | 26.2308 | 635.781 | 30.3542 | 635.781 | 40.6474 | 638.329 | 50.5991 | 635.781 | 60.3967 | 635.781 | 80.8773 | 636.417 | 100.678 | 637.691 | 130.573 | 637.053 | 162.541 | 636.417 | 202.336 | 636.417 | 276.699 | 634.51 | 333.93 | 634.51 | 382.195 | 634.51 | 437.874 | 634.51 | 545.079 | 633.876 | 657.162 | 631.346 | 880.008 | 635.145 | 976.457 | 571.837 | 1178.42 | 571.265 | 1562.32 | 572.981