## 176_22
S&C Power Fuses - Type SMU-20 (14.4 kV) | [9 empty] | S&C Power Fuses - Type SMU-20 (14.4 kV)
Very Slow Speed (TCC 176-2-2) | [9 empty] | Very Slow Speed (TCC 176-2-2)
Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
50E |  | 65E |  | 80E |  | 100E |  | 125E |  | 150E |  | 175E |  | 200E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
18451.9 | 0.024794 | 18359.9 | 0.024893 | 18451.9 | 0.025093 | 18674.7 | 0.025093 | 18433.5 | 0.032805 | 18581.6 | 0.032805 | 18618.8 | 0.033003 | 18268.3 | 0.033003
17604.8 | 0.024794 | 17308 | 0.024993 | 17763.9 | 0.025194 | 18104.7 | 0.025295 | 17604.8 | 0.033102 | 17996.4 | 0.033201 | 17835.1 | 0.033906 | 17517 | 0.034212
16496.8 | 0.024893 | 16202.6 | 0.025295 | 16796.5 | 0.025396 | 17325.3 | 0.025498 | 16999.3 | 0.033501 | 17084.5 | 0.034212 | 16999.3 | 0.035008 | 16596.1 | 0.035895
15614 | 0.024893 | 15289.5 | 0.025396 | 15913.5 | 0.025702 | 16447.4 | 0.025909 | 16349 | 0.033906 | 16414.6 | 0.035008 | 16186.4 | 0.036183 | 15723.7 | 0.037584
14822.8 | 0.024993 | 14660.7 | 0.025498 | 15137.4 | 0.025909 | 15304.8 | 0.026406 | 15786.7 | 0.034315 | 15723.7 | 0.035787 | 15536.1 | 0.03721 | 14956.8 | 0.039393
13848.4 | 0.025093 | 13890 | 0.025805 | 14298.7 | 0.0263 | 14370.4 | 0.026993 | 15182.9 | 0.034799 | 15107.2 | 0.036693 | 14719.4 | 0.039001 | 14085.8 | 0.041787
13055 | 0.025194 | 13041.9 | 0.026091 | 13547.1 | 0.026805 | 13547.1 | 0.027594 | 14456.9 | 0.035502 | 14442.4 | 0.037886 | 13931.7 | 0.041083 | 12976.9 | 0.045403
12123.8 | 0.025194 | 12039.2 | 0.026512 | 12643.8 | 0.027292 | 12899.2 | 0.028292 | 13820.7 | 0.036183 | 13820.7 | 0.039197 | 13199.4 | 0.043103 | 11883.7 | 0.04958
11135.8 | 0.025396 | 11069.2 | 0.027101 | 11730.2 | 0.027788 | 12087.5 | 0.0293 | 13292.1 | 0.036914 | 13199.4 | 0.040796 | 12393.5 | 0.045998 | 10970 | 0.054304
10341.5 | 0.0256 | 9926.15 | 0.027788 | 10926.3 | 0.028491 | 11315.4 | 0.030404 | 12809.3 | 0.037584 | 12493 | 0.042504 | 11625.1 | 0.048793 | 10126.6 | 0.059418
9594.33 | 0.025805 | 9053.69 | 0.028605 | 10167.2 | 0.029212 | 10435 | 0.031804 | 12245.6 | 0.03869 | 11601.9 | 0.045313 | 10785.1 | 0.052699 | 9479.89 | 0.064431
8990.54 | 0.026013 | 8151.26 | 0.029506 | 9310.78 | 0.030012 | 9556.03 | 0.033602 | 11636.8 | 0.039789 | 10550.4 | 0.049283 | 10015.8 | 0.056917 | 8847.83 | 0.070077
8424.74 | 0.0263 | 7215.08 | 0.030802 | 8690 | 0.03071 | 8838.99 | 0.03529 | 11191.7 | 0.040919 | 9536.94 | 0.054195 | 9236.59 | 0.062277 | 8332.58 | 0.075989
7950.01 | 0.026591 | 6528.47 | 0.031995 | 8086.31 | 0.031393 | 8249.67 | 0.036914 | 10656.5 | 0.042207 | 8577.76 | 0.060015 | 8475.44 | 0.068415 | 7769.24 | 0.083562
7427.38 | 0.026993 | 6032.57 | 0.033102 | 7517.04 | 0.032285 | 7730.49 | 0.03869 | 10187.6 | 0.04358 | 7592.59 | 0.068074 | 7839.48 | 0.074933 | 7243.99 | 0.092628
7008.84 | 0.027292 | 5635.99 | 0.03411 | 7072.21 | 0.033201 | 7316.8 | 0.04031 | 9681.07 | 0.045403 | 6727.29 | 0.078069 | 7236.75 | 0.082979 | 6587.49 | 0.10687
6502.41 | 0.027788 | 5276.02 | 0.035184 | 6600.68 | 0.034315 | 6987.85 | 0.041704 | 9282.89 | 0.04688 | 5948.7 | 0.090703 | 6640.4 | 0.092443 | 5919.03 | 0.12629
6068.87 | 0.028491 | 4909.5 | 0.03651 | 6197.67 | 0.035502 | 6620.51 | 0.043492 | 8909.99 | 0.048501 | 5371.85 | 0.10371 | 6081.02 | 0.10412 | 5387.99 | 0.14717
5669.91 | 0.029096 | 4614.36 | 0.037811 | 5819.26 | 0.036914 | 6310.23 | 0.045585 | 8517.92 | 0.050179 | 4870.38 | 0.11906 | 5579.91 | 0.11811 | 4894.8 | 0.17236
5377.23 | 0.029713 | 4367.42 | 0.039197 | 5496.84 | 0.038497 | 6008.49 | 0.047779 | 8110.61 | 0.052279 | 4398.1 | 0.13819 | 5156.06 | 0.13237 | 4433.43 | 0.2041
5038.83 | 0.030587 | 4121.32 | 0.040796 | 5104.76 | 0.040796 | 5692.63 | 0.05038 | 7784.8 | 0.054087 | 4051.85 | 0.1569 | 4759.64 | 0.15014 | 4031.64 | 0.24095
4750.13 | 0.031299 | 3904.67 | 0.042419 | 4778.72 | 0.043103 | 5420.42 | 0.053122 | 7434.81 | 0.056182 | 3721.67 | 0.18029 | 4398.1 | 0.17082 | 3673.6 | 0.28276
4500.43 | 0.032188 | 3714.24 | 0.044194 | 4451.2 | 0.045998 | 5135.48 | 0.056689 | 7129.01 | 0.058416 | 3425.24 | 0.20739 | 4072.16 | 0.19414 | 3384.39 | 0.32786
4217.21 | 0.033501 | 3414.98 | 0.048115 | 4187.79 | 0.048696 | 4831.58 | 0.061288 | 6876.93 | 0.060315 | 3130.44 | 0.24337 | 3744.07 | 0.22309 | 3090.01 | 0.38668
3971.62 | 0.034799 | 3209.69 | 0.051295 | 3889.08 | 0.053122 | 4559.32 | 0.066194 | 6594.08 | 0.062903 | 2826.88 | 0.29224 | 3428.67 | 0.25946 | 2821.23 | 0.4565
3755.32 | 0.036292 | 2971.82 | 0.056013 | 3626.16 | 0.057777 | 4280.94 | 0.072428 | 6272.49 | 0.06593 | 2580.99 | 0.34709 | 3171.4 | 0.29785 | 2588.74 | 0.54001
3522.51 | 0.038 | 2751.57 | 0.061719 | 3330.67 | 0.064818 | 3975.59 | 0.079965 | 5990.49 | 0.069172 | 2326.05 | 0.4193 | 2918.8 | 0.34536 | 2349.43 | 0.65236
3310.74 | 0.039908 | 2557.86 | 0.067802 | 3071.52 | 0.0725 | 3666.26 | 0.09007 | 5726.89 | 0.072573 | 2115.25 | 0.50401 | 2686.32 | 0.40488 | 2151.52 | 0.78415
3127.31 | 0.041997 | 2349.43 | 0.075837 | 2872.47 | 0.079566 | 3381 | 0.10145 | 5513.35 | 0.075837 | 1929.33 | 0.60825 | 2487.24 | 0.46947 | 1980.15 | 0.93038
2983.73 | 0.043886 | 2151.52 | 0.085506 | 2689.01 | 0.087496 | 3108.6 | 0.11577 | 5281.3 | 0.079726 | 1779.22 | 0.72097 | 2298.31 | 0.55037 | 1804.3 | 1.1284
2815.59 | 0.046599 | 1984.11 | 0.096408 | 2474.83 | 0.099444 | 2818.41 | 0.13586 | 5079.3 | 0.083729 | 1613.12 | 0.87971 | 2036.38 | 0.69966 | 1673.93 | 1.3442
2664.92 | 0.049481 | 1835.23 | 0.10914 | 2309.83 | 0.11112 | 2568.12 | 0.15753 | 4875.26 | 0.087934 | 1398.18 | 1.1816 | 1859.25 | 0.84861 | 1543.68 | 1.6142
2522.3 | 0.052593 | 1704.33 | 0.1233 | 2121.6 | 0.12629 | 2356.49 | 0.18302 | 4656.08 | 0.093559 | 1268.93 | 1.4577 | 1694.14 | 1.0231 | 1416.48 | 1.9559
2404.09 | 0.05579 | 1570.15 | 0.14183 | 1962.41 | 0.14282 | 2155.82 | 0.21264 | 4455.65 | 0.099245 | 1152.77 | 1.7804 | 1548.32 | 1.2534 | 1284.25 | 2.4592
2268.62 | 0.060315 | 1412.23 | 0.16997 | 1816.97 | 0.16119 | 1980.15 | 0.2473 | 4272.39 | 0.10496 | 1058.84 | 2.153 | 1403.78 | 1.5401 | 1180.78 | 3.0278
2149.37 | 0.064689 | 1279.12 | 0.20287 | 1718.02 | 0.17708 | 1815.16 | 0.29137 | 4100.76 | 0.11179 | 985.285 | 2.5417 | 1291.97 | 1.8383 | 1102.05 | 3.6395
2008.07 | 0.070923 | 1159.71 | 0.23951 | 1605.08 | 0.19906 | 1685.69 | 0.33348 | 3939.97 | 0.11799 | 915.006 | 3.0157 | 1158.55 | 2.3557 | 1051.45 | 4.1531
1891.13 | 0.076906 | 1074.84 | 0.27276 | 1507.08 | 0.2222 | 1551.42 | 0.39017 | 3796.85 | 0.12504 | 859.999 | 3.5143 | 1059.9 | 2.9237 | 1005.18 | 4.7391
1775.66 | 0.084318 | 993.199 | 0.31469 | 1426.43 | 0.24459 | 1435.01 | 0.45061 | 3629.78 | 0.13383 | 815.606 | 3.9902 | 989.234 | 3.5038 | 948.546 | 5.5948
1655.61 | 0.093465 | 918.674 | 0.36452 | 1315.44 | 0.28332 | 1327.33 | 0.52248 | 3470.06 | 0.14411 | 771.959 | 4.6221 | 930.694 | 4.1406 | 898.683 | 6.5853
1554.53 | 0.10288 | 852.293 | 0.4193 | 1233.89 | 0.31754 | 1211.88 | 0.62241 | 3334 | 0.15333 | 740.948 | 5.1595 | 867.774 | 5.0171 | 858.28 | 7.7125
1468.4 | 0.11246 | 798.656 | 0.47466 | 1149.32 | 0.36271 | 1119.82 | 0.72313 | 3196.87 | 0.16412 | 702.701 | 5.9945 | 822.979 | 5.9053 | 828.76 | 8.7045
1377.36 | 0.12367 | 732.843 | 0.5559 | 1064.14 | 0.42056 | 1040.99 | 0.8343 | 3050.1 | 0.17637 | 671.109 | 6.8747 | 784.409 | 6.8884 | 801.857 | 9.8833
1282.96 | 0.13888 | 683.298 | 0.6388 | 977.434 | 0.49601 | 966.741 | 0.97223 | 2927.57 | 0.1903 | 641.578 | 7.8605 | 753.652 | 7.8841 | 774.278 | 11.2666
1201.02 | 0.1541 | 634.559 | 0.7407 | 899.583 | 0.58149 | 906.808 | 1.115 | 2784.79 | 0.20739 | 610.288 | 9.2336 | 720.49 | 9.0961 | 752.146 | 12.8693
1114.24 | 0.17427 | 588.708 | 0.85713 | 841.285 | 0.66023 | 856.566 | 1.2634 | 2643.68 | 0.22669 | 585.772 | 10.8032 | 694.319 | 10.3381 | 726.277 | 14.8774
1037.87 | 0.19708 | 548.36 | 0.99485 | 778.938 | 0.77479 | 805.877 | 1.4432 | 2540.02 | 0.24216 | 563.931 | 12.4515 | 669.768 | 11.5518 | 704.812 | 17.1473
973.532 | 0.21977 | 512.311 | 1.1432 | 729.917 | 0.89033 | 754.406 | 1.6734 | 2428.25 | 0.26233 | 546.717 | 14.0953 | 648.026 | 13.1292 | 686.037 | 19.7044
912.265 | 0.2468 | 481.512 | 1.2928 | 683.298 | 1.0241 | 706.223 | 1.9364 | 2323.73 | 0.28389 | 531.09 | 15.9242 | 631.395 | 14.7441 | 667.094 | 22.9391
851.442 | 0.27827 | 453.018 | 1.4679 | 637.103 | 1.1839 | 667.094 | 2.2052 | 2230.38 | 0.306 | 515.394 | 18.4275 | 618.892 | 16.2785 | 653.231 | 26.0455
791.501 | 0.31722 | 427.063 | 1.6634 | 595.816 | 1.37 | 631.395 | 2.4914 | 2147.22 | 0.32655 | 504.683 | 20.7354 | 604.82 | 18.5569 | 639.017 | 29.9895
731.378 | 0.36782 | 394.229 | 1.9795 | 546.717 | 1.6484 | 591.068 | 2.8975 | 2044.54 | 0.35874 | 493.208 | 23.4025 | 589.887 | 21.2604 | 625.738 | 34.4961
677.176 | 0.42521 | 370.529 | 2.2679 | 511.287 | 1.9114 | 559.437 | 3.2964 | 1937.06 | 0.39488 | 482.476 | 27.4357 | 577.051 | 24.4308 | 615.19 | 39.3638
626.99 | 0.49403 | 352.106 | 2.5519 | 474.818 | 2.2679 | 528.441 | 3.7729 | 1846.28 | 0.43164 | 471.506 | 31.7803 | 566.191 | 27.5457 | 603.612 | 46.9859
584.602 | 0.56487 | 329.617 | 2.9738 | 446.273 | 2.6139 | 498.165 | 4.3572 | 1766.8 | 0.47135 | 462.169 | 37.2945 | 555.535 | 31.3071 | 592.251 | 55.3042
544.534 | 0.64975 | 310.422 | 3.4378 | 416.519 | 3.0828 | 471.506 | 5.002 | 1700.93 | 0.50653 | 452.565 | 44.6051 | 544.534 | 35.7248 | 581.686 | 66.4101
512.311 | 0.72749 | 292.052 | 3.9942 | 391.479 | 3.5853 | 446.72 | 5.7422 | 1632.6 | 0.55258 | 443.604 | 53.1356 | 535.356 | 41.8816 | 573.026 | 79.2692
481.994 | 0.8227 | 272.58 | 4.706 | 369.788 | 4.12 | 424.508 | 6.6715 | 1559.2 | 0.61008 | 433.951 | 64.0618 | 525.28 | 49.3949 | 563.931 | 96.4331
441.833 | 0.98102 | 260.586 | 5.2848 | 353.517 | 4.6779 | 406.641 | 7.4771 | 1465.46 | 0.69687 | 425.784 | 78.5589 | 515.394 | 58.5481 | 557.761 | 114.76
417.352 | 1.0995 | 250.869 | 5.8348 | 339.655 | 5.2218 | 391.87 | 8.3049 | 1380.12 | 0.78729 | 419.444 | 94.9025 | 507.213 | 69.5363 | 553.871 | 136.435
393.441 | 1.2409 | 241.515 | 6.4938 | 325.36 | 5.8407 | 375.002 | 9.4863 | 1303.65 | 0.88944 | 412.374 | 121.007 | 499.162 | 81.5201 | 549.457 | 169.839
371.271 | 1.388 | 232.509 | 7.2779 | 312.602 | 6.5394 | 356.713 | 10.9555 | 1216.74 | 1.0313 | 406.641 | 151.388 | 494.195 | 93.4895 | 543.446 | 213.119
344.444 | 1.6158 | 224.737 | 8.1567 | 299.146 | 7.4175 | 344.444 | 12.3153 | 1143.59 | 1.1816 | 402.193 | 197.127 | 489.768 | 108.945 | 536.964 | 272.558
323.737 | 1.8383 | 218.313 | 8.9607 | 285.126 | 8.5493 | 332.264 | 13.9272 | 1073.77 | 1.3523 | 398.191 | 271.198 | 483.926 | 127.593 | 532.153 | 350.672
301.549 | 2.1401 | 211.438 | 9.8734 | 274.494 | 9.7167 | 320.195 | 15.8924 | 1001.17 | 1.5775 | 393.835 | 399.755 | 475.768 | 153.984 | 528.441 | 433.05
279.48 | 2.4964 | 205.6 | 10.9227 | 263.204 | 11.2216 | 309.492 | 18.2807 | 943.816 | 1.8073 | 391.87 | 546.128 | 470.093 | 190.347 | 526.331 | 520.533
257.477 | 2.9857 | 200.523 | 11.9752 | 252.631 | 12.9079 | 299.146 | 21.0278 | 883.535 | 2.104 | 391.087 | 604.169 | 464.486 | 242.221 | 525.805 | 601.757
239.83 | 3.5213 | 194.208 | 13.4347 | 245.165 | 14.6559 | 291.177 | 24.1877 | 822.979 | 2.479 |  |  | 459.864 | 304.555
224.737 | 4.0994 | 189.224 | 15.1628 | 237.919 | 16.7073 | 282.854 | 28.1021 | 782.842 | 2.7866 |  |  | 457.571 | 400.155
211.438 | 4.7915 | 182.898 | 17.3891 | 230.657 | 19.4111 | 273.946 | 33.5101 | 747.647 | 3.1076 |  |  | 455.288 | 480.512
200.123 | 5.5226 | 178.919 | 19.5474 | 224.288 | 22.3728 | 267.45 | 38.5073 | 714.749 | 3.5038 |  |  | 453.925 | 567.848
189.035 | 6.442 | 172.938 | 22.7336 | 217.442 | 26.3863 | 261.107 | 45.0533 | 683.298 | 3.9545 |  |  | 452.565 | 602.359
180.717 | 7.329 | 169.344 | 25.6065 | 212.285 | 31.0887 | 255.17 | 52.9235 | 649.323 | 4.5215
170.363 | 8.7045 | 167.324 | 28.074 | 206.63 | 37.519 | 249.119 | 62.7933 | 617.656 | 5.1492
164.668 | 9.6586 | 164.011 | 31.8439 | 201.126 | 45.5061 | 244.186 | 74.1321 | 584.602 | 6.0245
158.369 | 11.0767 | 161.246 | 36.483 | 196.16 | 57.5036 | 239.112 | 89.8237 | 557.204 | 6.8884
152.16 | 12.703 | 159.322 | 41.7979 | 192.276 | 72.0852 | 234.611 | 109.382 | 532.685 | 7.9157
147.663 | 14.5682 | 157.265 | 47.7437 | 187.716 | 92.1898 | 230.888 | 133.867 | 510.265 | 8.9876
143.299 | 16.5907 | 155.078 | 55.3042 | 183.815 | 115.105 | 227.45 | 160.91 | 489.278 | 10.3072
138.093 | 19.4111 | 153.689 | 64.3186 | 180.536 | 144.872 | 224.737 | 198.115 | 471.506 | 11.7499
135.088 | 21.7986 | 151.401 | 78.795 | 177.848 | 184.168 | 222.501 | 239.811 | 455.744 | 13.2479
131.358 | 25.301 | 150.345 | 95.3782 | 175.727 | 233.89 | 219.847 | 293.199 | 445.827 | 14.7441
127.604 | 30.0495 | 149.147 | 111.035 | 174.327 | 299.421 | 217.877 | 355.972 | 432.218 | 16.8078
124.702 | 34.8777 | 146.779 | 132.403 | 173.284 | 381.783 | 216.141 | 433.05 | 421.547 | 19.103
122.478 | 39.2459 | 145.028 | 165.977 | 172.938 | 469.587 | 215.278 | 602.359 | 411.139 | 21.7986
120.413 | 46.6115 | 143.585 | 208.065 | 172.765 | 605.378 |  |  | 399.387 | 25.2
118.502 | 55.3042 | 142.726 | 265.032 |  |  |  |  | 391.479 | 28.4414
116.621 | 66.7429 | 141.448 | 360.99 |  |  |  |  | 383.343 | 33.1435
114.885 | 80.2261 | 141.024 | 475.731 |  |  |  |  | 373.879 | 39.2852
113.514 | 95.0924 | 141.024 | 607.197 |  |  |  |  | 364.648 | 48.3201
112.385 | 114.531 | [6 empty] | 355.644 | 61.2429
111.713 | 151.995 | [6 empty] | 349.649 | 77.4668
110.933 | 210.156 | [6 empty] | 344.1 | 100.068
110.049 | 284.533 | [6 empty] | 339.655 | 130.954
109.501 | 396.173 | [6 empty] | 335.268 | 171.545
109.173 | 518.974 | [6 empty] | 331.269 | 211.421
109.173 | 574.128 | [6 empty] | 326.991 | 275.297
108.954 | 604.773 | [6 empty] | 323.09 | 403.369
[8 empty] | 322.122 | 599.954