## 690-9
S&C Vista Underground Distribution Switchgear Overcurrent Control | [13 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control
Main Interrupter Speed (TCC 690-9) | [13 empty] | Main Interrupter Speed (TCC 690-9)
Minimum Tripping Time-Current Characteristic Curves Dated February 16, 2009 | [13 empty] | Minimum Tripping Time-Current Characteristic Curves Dated February 16, 2009
Tolerance: | Curves are plotted to minimum test points. | [12 empty] | Tolerance: | Curves are plotted to minimum test points.
| Maximum variations are plus 10% in terms of current, plus 20% in terms of time, | [13 empty] | Maximum variations are plus 10% in terms of current, plus 20% in terms of time,
| or plus 6 milliseconds (60-Hz), plus 10 milliseconds (50-Hz), whichever is greater. | [13 empty] | or plus 6 milliseconds (60-Hz), plus 10 milliseconds (50-Hz), whichever is greater.
100A |  | 150A |  | 200A |  | 250A |  | 300A |  | 350A |  | 400A |  | 450A |  | 500A |  | 600A |  | 700A |  | 800A
CURRENT | TIME | CURRENT | TIME | CURRENT | TIME | CURRENT | TIME | CURRENT | TIME | CURRENT | TIME | CURRENT | TIME | CURRENT | TIME | CURRENT | TIME | CURRENT | TIME | CURRENT | TIME | CURRENT | TIME
16000 | 0.045 | 16000 | 0.0455 | 16000 | 0.0455 | 16000 | 0.0455 | 16000 | 0.0455 | 16000 | 0.0455 | 16000 | 0.0475 | 16000 | 0.0475 | 16000 | 0.0475 | 16000 | 0.0477 | 16000 | 0.0493 | 16000 | 0.0521
15270.106 | 0.045 | 8500 | 0.0456 | 15270.106 | 0.0455 | 14000.247 | 0.0455 | 14891.846 | 0.0455 | 13699.59 | 0.0456 | 14918.188 | 0.0476 | 15914.78 | 0.0475 | 15472.571 | 0.0477 | 15473.506 | 0.0478 | 15096.55 | 0.05 | 15363.847 | 0.0525
12406.845 | 0.045 | 4320.05 | 0.0459 | 12406.845 | 0.0455 | 12212.246 | 0.0456 | 12990.163 | 0.0455 | 11946.713 | 0.0455 | 12983.748 | 0.0477 | 11431.828 | 0.0481 | 14322.568 | 0.0482 | 13939.216 | 0.0491 | 13416.61 | 0.0518 | 13413.765 | 0.055
9528.171 | 0.045 | 3974.242 | 0.0464 | 9528.171 | 0.0455 | 10630.395 | 0.0455 | 11155.44 | 0.0456 | 10705.09 | 0.0454 | 11806.774 | 0.0479 | 12610.217 | 0.0477 | 13093.028 | 0.0487 | 12543.954 | 0.0506 | 11898.73 | 0.0537 | 11338.204 | 0.0591
7565.874 | 0.0451 | 3721.514 | 0.0466 | 7565.874 | 0.0455 | 9647.669 | 0.0455 | 9904.958 | 0.0456 | 9693.287 | 0.0455 | 10691.74 | 0.0479 | 13751.294 | 0.0476 | 12006.575 | 0.0496 | 11300.147 | 0.0522 | 10519.58 | 0.0565 | 9961.293 | 0.063
6001.441 | 0.0452 | 3409.364 | 0.0477 | 6001.441 | 0.0455 | 7938.079 | 0.046 | 8640.099 | 0.0459 | 8934.452 | 0.0459 | 9938.094 | 0.0479 | 14716.542 | 0.0476 | 11033.281 | 0.0504 | 10094.985 | 0.054 | 9707.025 | 0.0587 | 8936.271 | 0.0665
5004.905 | 0.0455 | 3024.032 | 0.0495 | 5474.905 | 0.0455 | 6795.504 | 0.0463 | 7948.483 | 0.0464 | 8352.64 | 0.0468 | 9227.931 | 0.0489 | 10907.338 | 0.0483 | 10086.115 | 0.0515 | 9295.631 | 0.056 | 8892.008 | 0.0612 | 7892.145 | 0.0719
4126.571 | 0.0462 | 2776.17 | 0.0508 | 5126.571 | 0.0455 | 6090.584 | 0.0472 | 7443.027 | 0.0466 | 7334.596 | 0.0482 | 8470.656 | 0.0501 | 9734.483 | 0.0496 | 9326.722 | 0.0529 | 8149.621 | 0.0593 | 8162.447 | 0.0638 | 6962.742 | 0.0782
2397.696 | 0.047 | 2488.218 | 0.0529 | 5000 | 0.0457 | 5709.187 | 0.0479 | 6750.729 | 0.0477 | 6570.906 | 0.0496 | 7543.591 | 0.0527 | 8954.714 | 0.051 | 8437.535 | 0.0548 | 7356.886 | 0.0627 | 7461.519 | 0.0673 | 6170.942 | 0.0852
2285.327 | 0.0474 | 2244.131 | 0.0551 | 4570.654 | 0.0468 | 5379.656 | 0.0489 | 5900.064 | 0.0495 | 5925.029 | 0.0513 | 6788.506 | 0.0545 | 8332.521 | 0.0522 | 7721.259 | 0.057 | 6620.49 | 0.0662 | 6778.19 | 0.0713 | 5482.725 | 0.0954
2212.586 | 0.0476 | 2049.478 | 0.0576 | 4425.171 | 0.0476 | 4950.454 | 0.05 | 5490.34 | 0.0508 | 5501.29 | 0.053 | 6109.003 | 0.057 | 7538.119 | 0.0543 | 7162.309 | 0.059 | 5951.586 | 0.0709 | 6241.579 | 0.0754 | 4940.639 | 0.1049
2100.108 | 0.0482 | 1863.917 | 0.0602 | 4200.216 | 0.0482 | 4603.071 | 0.0513 | 4966.435 | 0.0529 | 4970.928 | 0.0559 | 5660.627 | 0.0588 | 6948.777 | 0.056 | 6418.894 | 0.062 | 5480.32 | 0.0752 | 5658.145 | 0.0806 | 4448.85 | 0.1171
1999.598 | 0.0491 | 1682.826 | 0.0636 | 3999.196 | 0.0491 | 4222.232 | 0.0531 | 4488.262 | 0.0551 | 4515.231 | 0.0589 | 5169.038 | 0.0614 | 6385.485 | 0.0582 | 5892.404 | 0.065 | 4993.949 | 0.0805 | 5150.713 | 0.0872 | 4079.537 | 0.1295
1880.207 | 0.0502 | 1491.074 | 0.0682 | 3760.414 | 0.0502 | 3842.005 | 0.0547 | 4070.956 | 0.0576 | 4157.41 | 0.0615 | 4730.008 | 0.0641 | 5898.557 | 0.0603 | 5448.76 | 0.0677 | 4555.497 | 0.0868 | 4772.749 | 0.0934 | 3748.702 | 0.1449
1756.91 | 0.0514 | 1339.206 | 0.0737 | 3513.821 | 0.0514 | 3460.546 | 0.0576 | 3727.834 | 0.0602 | 3721.439 | 0.0657 | 4305.728 | 0.0678 | 5386.563 | 0.0632 | 4970.617 | 0.0715 | 4164.227 | 0.0943 | 4413.295 | 0.1012 | 3433.924 | 0.1642
1639.988 | 0.0529 | 1190.327 | 0.0799 | 3279.975 | 0.0529 | 3163.65 | 0.0603 | 3365.653 | 0.0636 | 3412.23 | 0.0694 | 3956.514 | 0.0713 | 4873.021 | 0.0668 | 4693.327 | 0.0746 | 3767.021 | 0.1036 | 4110.846 | 0.1082 | 3148.863 | 0.1867
1514.954 | 0.0545 | 1083.684 | 0.087 | 3029.909 | 0.0545 | 2898.266 | 0.0633 | 2982.149 | 0.0682 | 3122.18 | 0.0744 | 3669.953 | 0.0749 | 4459.342 | 0.0704 | 4349.03 | 0.0789 | 3501.489 | 0.1108 | 3805.213 | 0.1175 | 2973.129 | 0.204
1384.928 | 0.057 | 1001.106 | 0.0936 | 2769.855 | 0.057 | 2688.586 | 0.0661 | 2678.413 | 0.0737 | 2889.817 | 0.0787 | 3361.756 | 0.0799 | 4114.996 | 0.0747 | 3988.15 | 0.0839 | 3200.748 | 0.1229 | 3514.957 | 0.1301 | 2706.467 | 0.2371
1254.226 | 0.0598 | 920.97 | 0.102 | 2508.453 | 0.0598 | 2460.485 | 0.0696 | 2380.654 | 0.0799 | 2646.939 | 0.0849 | 3108.518 | 0.0846 | 3849.111 | 0.0779 | 3676.35 | 0.0892 | 2959.639 | 0.1362 | 3308.433 | 0.1417 | 2505.226 | 0.2717
1098.559 | 0.0646 | 849.904 | 0.1103 | 2197.118 | 0.0646 | 2284.858 | 0.0734 | 2167.368 | 0.087 | 2437.176 | 0.0915 | 2901.497 | 0.09 | 3585.407 | 0.0822 | 3445.993 | 0.0953 | 2719.599 | 0.1543 | 3033.817 | 0.1587 | 2278.151 | 0.3197
973.32 | 0.0696 | 793.371 | 0.1198 | 1946.641 | 0.0696 | 2119.555 | 0.0775 | 2002.211 | 0.0936 | 2237.011 | 0.0993 | 2627.479 | 0.0984 | 3332.805 | 0.0875 | 3146.881 | 0.1035 | 2491.211 | 0.1743 | 2837.731 | 0.1763 | 2073.822 | 0.3745
870.496 | 0.0751 | 729.103 | 0.1349 | 1740.992 | 0.0751 | 1962.115 | 0.0821 | 1830.54 | 0.102 | 2070.525 | 0.1075 | 2419.427 | 0.106 | 3062.637 | 0.0945 | 2906.914 | 0.112 | 2303.551 | 0.1964 | 2626.752 | 0.1976 | 1937.746 | 0.428
775.292 | 0.0823 | 679.896 | 0.1478 | 1550.583 | 0.0823 | 1848.862 | 0.0864 | 1702.807 | 0.1103 | 1924.458 | 0.1175 | 2186.365 | 0.119 | 2808.5 | 0.1021 | 2716.252 | 0.1208 | 2105.7 | 0.2285 | 2459.543 | 0.2205 | 1818.176 | 0.4937
681.907 | 0.0921 | 636.66 | 0.1639 | 1363.814 | 0.0921 | 1740.331 | 0.0913 | 1596.742 | 0.1198 | 1768.25 | 0.1299 | 2055.729 | 0.1288 | 2632.522 | 0.1093 | 2540.745 | 0.1305 | 1940.989 | 0.2632 | 2271.932 | 0.254 | 1718.499 | 0.5589
620.783 | 0.1024 | 593.074 | 0.1826 | 1241.566 | 0.1024 | 1611.059 | 0.0982 | 1458.206 | 0.1349 | 1645.225 | 0.142 | 1924.842 | 0.1398 | 2444.501 | 0.1185 | 2369.149 | 0.1445 | 1825.015 | 0.2917 | 2142.913 | 0.2812 | 1631.085 | 0.6355
552.312 | 0.1169 | 553.624 | 0.2042 | 1104.625 | 0.1169 | 1486.73 | 0.1076 | 1359.792 | 0.1478 | 1532.361 | 0.1578 | 1815.511 | 0.1532 | 2332.348 | 0.1255 | 2186.205 | 0.1627 | 1698.145 | 0.3308 | 2004.409 | 0.3159 | 1551.353 | 0.7165
497.586 | 0.1351 | 513.04 | 0.2296 | 995.172 | 0.1351 | 1335.289 | 0.1219 | 1273.321 | 0.1639 | 1439.222 | 0.175 | 1682.26 | 0.1697 | 2183.925 | 0.1359 | 2006.888 | 0.1853 | 1575.152 | 0.3764 | 1847.653 | 0.3662 | 1470.904 | 0.8215
445.484 | 0.1574 | 489.519 | 0.2533 | 890.968 | 0.1574 | 1232.242 | 0.1356 | 1186.147 | 0.1826 | 1357.408 | 0.1912 | 1590.025 | 0.1856 | 2075.046 | 0.1457 | 1869.396 | 0.2085 | 1484.133 | 0.426 | 1722.829 | 0.4202 | 1400.464 | 0.945
408.526 | 0.1818 | 459.826 | 0.2815 | 817.051 | 0.1818 | 1139.522 | 0.1519 | 1100.249 | 0.2042 | 1276.236 | 0.211 | 1495.021 | 0.2032 | 1947.056 | 0.1594 | 1728.647 | 0.2359 | 1378.078 | 0.4988 | 1616.532 | 0.4838 | 1333.397 | 1.0757
372.294 | 0.2063 | 431.034 | 0.3148 | 744.589 | 0.2063 | 1069.279 | 0.1669 | 1026.08 | 0.2296 | 1181.254 | 0.239 | 1411.577 | 0.2259 | 1836.52 | 0.1756 | 1563.842 | 0.2774 | 1313.448 | 0.5564 | 1516.793 | 0.5529 | 1268.217 | 1.2362
329.508 | 0.253 | 403.204 | 0.3562 | 659.016 | 0.253 | 990.886 | 0.1875 | 979.038 | 0.2533 | 1108.297 | 0.2676 | 1334.183 | 0.2464 | 1698.247 | 0.198 | 1467.384 | 0.3094 | 1232.392 | 0.6481 | 1418.758 | 0.6488 | 1212.537 | 1.4494
295.314 | 0.3057 | 381.522 | 0.3997 | 590.627 | 0.3057 | 926.805 | 0.2077 | 919.652 | 0.2815 | 1044.202 | 0.2949 | 1272.939 | 0.2685 | 1576.954 | 0.2228 | 1365.427 | 0.3553 | 1147.918 | 0.7751 | 1342.387 | 0.7416 | 1170.247 | 1.6553
262.194 | 0.3832 | 355.772 | 0.4614 | 524.387 | 0.3832 | 867.671 | 0.2286 | 862.069 | 0.3148 | 978.687 | 0.3323 | 1191.892 | 0.2994 | 1487.429 | 0.2469 | 1283.884 | 0.3946 | 1069.233 | 0.9271 | 1259.563 | 0.8603 | 1117.701 | 1.9085
237.697 | 0.4645 | 333.496 | 0.5282 | 475.394 | 0.4645 | 819.561 | 0.2533 | 806.407 | 0.3562 | 920.162 | 0.3768 | 1114.84 | 0.3391 | 1365.427 | 0.2853 | 1210.997 | 0.4429 | 1010.609 | 1.0801 | 1180.794 | 1.0096 | 1074.222 | 2.2473
220.494 | 0.5506 | 318.871 | 0.5938 | 440.987 | 0.5506 | 777.916 | 0.2779 | 763.043 | 0.3997 | 860.628 | 0.425 | 1069.233 | 0.3677 | 1254.741 | 0.3284 | 1144.634 | 0.5024 | 948.243 | 1.2824 | 1106.616 | 1.2386 | 1035.674 | 2.5477
204.108 | 0.6695 | 302.985 | 0.6705 | 408.217 | 0.6695 | 725.409 | 0.3099 | 711.545 | 0.4614 | 799.915 | 0.5001 | 1029.785 | 0.3995 | 1198.424 | 0.3598 | 1072.912 | 0.5796 | 898.126 | 1.499 | 1047.048 | 1.4584 | 994.348 | 2.9624
186.98 | 0.8322 | 284.607 | 0.7773 | 373.96 | 0.8322 | 676.446 | 0.3566 | 668.992 | 0.5282 | 760.776 | 0.5624 | 981.488 | 0.44 | 1123.332 | 0.4098 | 1022.62 | 0.6555 | 856.005 | 1.7392 | 985.528 | 1.7688 | 957.666 | 3.5592
172.905 | 1.0302 | 268.741 | 0.9088 | 345.81 | 1.0302 | 634.749 | 0.4052 | 637.742 | 0.5938 | 731.155 | 0.6133 | 919.958 | 0.5039 | 1056.247 | 0.4663 | 968.6 | 0.7437 | 826.147 | 1.9696 | 941.28 | 2.1227 | 924.265 | 4.2269
157.406 | 1.3488 | 255.62 | 1.0315 | 314.813 | 1.3488 | 596.141 | 0.4604 | 605.97 | 0.6705 | 699.024 | 0.678 | 878.646 | 0.5562 | 1018.359 | 0.5099 | 918.391 | 0.8492 | 798.163 | 2.233 | 899.019 | 2.5103 | 892.029 | 4.9777
141.219 | 1.8754 | 239 | 1.254 | 285.38 | 1.8754 | 569.498 | 0.5079 | 569.214 | 0.7773 | 664.128 | 0.7729 | 836.564 | 0.627 | 958.543 | 0.584 | 871.695 | 0.9789 | 771.127 | 2.5774 | 858.655 | 3.0351 | 869.046 | 5.893
134.6 | 2.2996 | 226.02 | 1.4584 | 269.201 | 2.2996 | 539.995 | 0.5723 | 537.482 | 0.9088 | 637.603 | 0.8618 | 793.178 | 0.7077 | 916.476 | 0.6515 | 831.702 | 1.1037 | 746.564 | 2.9686 | 824.396 | 3.5781 | 847.539 | 6.9546
125.906 | 2.9508 | 215 | 1.6997 | 251.811 | 2.9508 | 513.626 | 0.6434 | 511.239 | 1.0315 | 607.04 | 0.9731 | 763.116 | 0.787 | 874.429 | 0.7292 | 786.945 | 1.298 | 716.771 | 3.4302 | 796.478 | 4.2945 | 829.158 | 8.3034
121.137 | 3.524 | 205.556 | 2.0189 | 242.274 | 3.524 | 490.076 | 0.7334 | 477.246 | 1.254 | 585.237 | 1.0736 | 730.371 | 0.8799 | 836.926 | 0.8196 | 742.27 | 1.5171 | 688.886 | 4.1258 | 768.701 | 5.1004 | 818.833 | 9.8616
115.46 | 4.418 | 196.747 | 2.3604 | 230.92 | 4.418 | 468.173 | 0.8246 | 454.041 | 1.4584 | 565.988 | 1.1794 | 694.665 | 0.9859 | 801.869 | 0.9241 | 703.059 | 1.8455 | 667.64 | 4.8179 | 744.999 | 6.2393 | 808.638 | 11.3234
111.436 | 5.4402 | 189.892 | 2.7249 | 220.871 | 5.4402 | 446.165 | 0.938 | 431.119 | 1.6997 | 543.382 | 1.315 | 669.036 | 1.1023 | 771.494 | 1.0182 | 674.313 | 2.1299 | 648.402 | 5.8503 | 728.843 | 7.2785 | 800 | 13.4
110 | 5.8973 | 181.754 | 3.2503 | 210.87 | 7.0326 | 422.17 | 1.0863 | 411.113 | 2.0189 | 521.68 | 1.4833 | 624.479 | 1.3409 | 741.496 | 1.1289 | 644.72 | 2.5426 | 631.694 | 7.0072 | 717.518 | 8.473 | 800 | 16.5385
105.2 | 7.8 | 173.422 | 3.9598 | 203.909 | 9.246 | 400.717 | 1.2594 | 393.494 | 2.3604 | 506.106 | 1.6591 | 600.185 | 1.4743 | 714.898 | 1.2663 | 622.893 | 2.9407 | 613.491 | 8.5089 | 707.845 | 9.8845 | 800 | 19.5185
103.2 | 9.4 | 166.857 | 4.8908 | 200 | 13.4 | 376.801 | 1.5054 | 379.785 | 2.7249 | 488.948 | 1.846 | 582.282 | 1.633 | 682.099 | 1.4356 | 602.433 | 3.3869 | 603.957 | 10.3434 | 702 | 11.6904 | 800 | 23.2554
101.2 | 11.4 | 164 | 5.2599 | 200 | 13.4537 | 358.028 | 1.76 | 363.509 | 3.2503 | 476.339 | 2.0625 | 558.461 | 1.8708 | 661.763 | 1.5784 | 586.305 | 3.7914 | 601 | 11.9524 | 700 | 13.4 | 800 | 27.0434
100 | 13.4 | 161 | 6 | 200 | 18.2192 | 341.968 | 2.106 | 346.843 | 3.9598 | 458.75 | 2.3413 | 536.175 | 2.166 | 644.72 | 1.7595 | 571.802 | 4.3439 | 600 | 13.4 | 700 | 15.7097 | 800 | 33.7524
100 | 600 | 157 | 7 | 200 | 24.9876 | 329.022 | 2.4184 | 332.714 | 4.8908 | 447.386 | 2.616 | 522.359 | 2.4272 | 615.14 | 2.0351 | 557.075 | 4.9927 | 600 | 18.1345 | 700 | 18.6587 | 800 | 41.1159
|  | 155.3 | 7.8 | 200 | 38.5345 | 318.586 | 2.6962 | 321.098 | 5.9458 | 433.124 | 2.9727 | 505.192 | 2.7575 | 600.55 | 2.2566 | 541.032 | 5.787 | 600 | 21.5615 | 700 | 21.0889 | 800 | 50.7241
|  | 153 | 9.4 | 200 | 74.266 | 309.741 | 3.0604 | 312.145 | 7.003 | 416.695 | 3.4943 | 490.123 | 3.1693 | 579.613 | 2.5992 | 527.648 | 6.8797 | 600 | 25.4475 | 700 | 24.8634 | 800 | 66.8798
|  | 151.8 | 10.4 | 200 | 126.7547 | 299.854 | 3.4556 | 307.007 | 8.1961 | 407.649 | 3.8919 | 474.511 | 3.658 | 565.865 | 2.8701 | 519.994 | 8.093 | 600 | 30.5132 | 700 | 29.9074 | 800 | 80.1066
|  | 151.2 | 11.4 | 200 | 221.428 | 293.052 | 3.9265 | 303.53 | 9.5521 | 396.307 | 4.404 | 461.802 | 4.1254 | 548.995 | 3.3024 | 512.987 | 9.2237 | 600 | 35.4096 | 700 | 35.0749 | 800 | 93.7474
|  | 150 | 13.4 | 200 | 313.1358 | 286.404 | 4.3915 | 302.52 | 10.9344 | 388.109 | 4.8844 | 450.372 | 4.6918 | 532.628 | 3.7878 | 506.074 | 10.6689 | 600 | 43.5479 | 700 | 42.5035 | 800 | 109.1335
|  | 150 | 600 | 200 | 458.0531 | 273.557 | 5.6341 | 300 | 13.4 | 377.705 | 5.6213 | 440.603 | 5.3249 | 517.288 | 4.3722 | 501.342 | 12.8183 | 600 | 51.2885 | 700 | 50.75 | 800 | 132.104
|  |  |  | 200 | 600 | 262.653 | 7.0923 | 300 | 15.8228 | 371.83 | 6.4421 | 432.399 | 6.0754 | 505.546 | 5.0097 | 500 | 13.4 | 600 | 62.3483 | 700 | 58.0913 | 800 | 160.7554
[6 empty] | 255.892 | 8.6313 | 300 | 18.0934 | 361.863 | 7.4297 | 422.905 | 6.8372 | 494.586 | 5.5321 | 500 | 15.352 | 600 | 78.4797 | 700 | 78.5626 | 800 | 192.9554
[6 empty] | 252 | 10.4601 | 300 | 21.514 | 356.606 | 8.1364 | 416.063 | 7.9589 | 485.888 | 6.4128 | 500 | 18.9178 | 600 | 102.9364 | 700 | 100.9992 | 800 | 238.2997
[6 empty] | 251 | 12.0625 | 300 | 25.1263 | 354.377 | 9.0431 | 410.12 | 9.5121 | 480.351 | 7.2249 | 500 | 22.8254 | 600 | 129.7065 | 700 | 123.6896 | 800 | 288.1532
[6 empty] | 250 | 13.4 | 300 | 30.0982 | 351.427 | 10.309 | 406.139 | 11.0145 | 471.859 | 8.482 | 500 | 28.1273 | 600 | 165.5219 | 700 | 148.6268 | 800 | 354.7442
[6 empty] | 250 | 13.6342 | 300 | 34.7825 | 350.9 | 11.4698 | 400 | 13.4 | 461.535 | 9.8532 | 500 | 35.0285 | 600 | 205.726 | 700 | 184.7272 | 800 | 429.8652
[6 empty] | 250 | 15.2972 | 300 | 43.2793 | 350 | 13.4 | 400 | 15.5849 | 456.702 | 10.778 | 500 | 41.6445 | 600 | 259.5022 | 700 | 221.0353 | 800 | 514.8819
[6 empty] | 250 | 19.8551 | 300 | 53.5116 | 350 | 14.9372 | 400 | 17.7071 | 453.043 | 12.6267 | 500 | 50.1937 | 600 | 319.4842 | 700 | 259.7763 | 800 | 572.1912
[6 empty] | 250 | 25.2593 | 300 | 64.2358 | 350 | 18.1424 | 400 | 19.9071 | 450 | 13.4 | 500 | 61.011 | 600 | 392.5012 | 700 | 316.7977 | 800 | 600
[6 empty] | 250 | 31.1325 | 300 | 78.9212 | 350 | 20.3568 | 400 | 22.6179 | 450 | 14.7457 | 500 | 72.7645 | 600 | 480.1745 | 700 | 379.0646
[6 empty] | 250 | 39.1075 | 300 | 98.3041 | 350 | 24.208 | 400 | 26.9757 | 450 | 16.95 | 500 | 89.3842 | 600 | 541.5753 | 700 | 462.7585
[6 empty] | 250 | 46.2561 | 300 | 121.4174 | 350 | 27.2201 | 400 | 30.7788 | 450 | 19.4018 | 500 | 106.4915 | 600 | 600 | 700 | 538.1562
[6 empty] | 250 | 55.001 | 300 | 153.9764 | 350 | 31.3268 | 400 | 35.453 | 450 | 23.3623 | 500 | 126.6038 |  |  | 700 | 600
[6 empty] | 250 | 65.3302 | 300 | 187.3889 | 350 | 38.0892 | 400 | 43.1404 | 450 | 27.5438 | 500 | 166.56
[6 empty] | 250 | 78.5886 | 300 | 238.6444 | 350 | 47.1507 | 400 | 47.941 | 450 | 32.7838 | 500 | 224.0351
[6 empty] | 250 | 94.8377 | 300 | 292.5842 | 350 | 55.2477 | 400 | 55.9255 | 450 | 37.7645 | 500 | 299.758
[6 empty] | 250 | 108.4467 | 300 | 365.9847 | 350 | 64.5986 | 400 | 63.8775 | 450 | 44.524 | 500 | 389.4007
[6 empty] | 250 | 129.7686 | 300 | 459.7367 | 350 | 76.5767 | 400 | 73.6563 | 450 | 50.4296 | 500 | 473.8231
[6 empty] | 250 | 150.2822 | 300 | 535.2294 | 350 | 88.1297 | 400 | 88.4068 | 450 | 57.7856 | 500 | 554.4769
[6 empty] | 250 | 181.5464 | 300 | 600 | 350 | 99.8311 | 400 | 102.6967 | 450 | 72.43 | 500 | 600
[6 empty] | 250 | 223.7587 |  |  | 350 | 116.8512 | 400 | 119.4223 | 450 | 91.8461
[6 empty] | 250 | 256.138 |  |  | 350 | 140.5823 | 400 | 134.6869 | 450 | 111.8881
[6 empty] | 250 | 306.8213 |  |  | 350 | 161.7918 | 400 | 151.4227 | 450 | 131.2213
[6 empty] | 250 | 369.0892 |  |  | 350 | 183.2736 | 400 | 174.9729 | 450 | 154.2204
[6 empty] | 250 | 426.5327 |  |  | 350 | 214.5198 | 400 | 201.7596 | 450 | 196.3898
[6 empty] | 250 | 497.0976 |  |  | 350 | 258.9055 | 400 | 234.372 | 450 | 231.5432
[6 empty] | 250 | 572.0427 |  |  | 350 | 307.2371 | 400 | 266.8519 | 450 | 275.5947
[6 empty] | 250 | 600 |  |  | 350 | 381.5366 | 400 | 307.3801 | 450 | 318.8105
[10 empty] | 350 | 435.8633 | 400 | 346.3045 | 450 | 377.4675
[10 empty] | 350 | 493.2133 | 400 | 403.5566 | 450 | 445.5037
[10 empty] | 350 | 547.5958 | 400 | 464.3568 | 450 | 508.3393
[10 empty] | 350 | 600 | 400 | 523.1596 | 450 | 579.4257
[12 empty] | 400 | 600 | 450 | 600